## SOLAR_INVERTER
Tag Name | PLC_Address | Source Device | Protocol | IP:Port | Unit ID | Register Type | Data Type | Unit | Scale | Status | Description / Notes
INVERTER_1.INV1_AC_POWER |  | Sineng SAU-100 (gateway for inverter 1) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | kW | TBC | TBC | Total active AC power
INVERTER_1.INV1_CURRENT_I1 |  | Sineng SAU-100 (gateway for inverter 1) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | AC phase current L1
INVERTER_1.INV1_CURRENT_I2 |  | Sineng SAU-100 (gateway for inverter 1) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | AC phase current L2
INVERTER_1.INV1_CURRENT_I3 |  | Sineng SAU-100 (gateway for inverter 1) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | AC phase current L3
INVERTER_1.INV1_DC_POWER |  | Sineng SAU-100 (gateway for inverter 1) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | kW | TBC | TBC | Total DC input power
INVERTER_1.INV1_FREKANS |  | Sineng SAU-100 (gateway for inverter 1) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | Hz | TBC | TBC | Grid frequency
INVERTER_1.INV1_VOLTAGE_V1 |  | Sineng SAU-100 (gateway for inverter 1) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | V | TBC | TBC | AC phase voltage L1
INVERTER_1.INV1_VOLTAGE_V2 |  | Sineng SAU-100 (gateway for inverter 1) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | V | TBC | TBC | AC phase voltage L2
INVERTER_1.INV1_VOLTAGE_V3 |  | Sineng SAU-100 (gateway for inverter 1) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | V | TBC | TBC | AC phase voltage L3
INVERTER_1.INV1_DAILY_PRODUCTION |  | Sineng SAU-100 (gateway for inverter 1) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | kWh | TBC | TBC | Energy today
INVERTER_1.INV1_Connection_Error |  | Sineng SAU-100 (gateway for inverter 1) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Boolean |  | TBC | TBC | 1 = inverter not responding on SAU RS485 bus
INVERTER_1.INV1_String_CURRENT_I1 |  | Sineng SAU-100 (gateway for inverter 1) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 1 current
INVERTER_1.INV1_String_CURRENT_I2 |  | Sineng SAU-100 (gateway for inverter 1) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 2 current
INVERTER_1.INV1_String_CURRENT_I3 |  | Sineng SAU-100 (gateway for inverter 1) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 3 current
INVERTER_1.INV1_String_CURRENT_I4 |  | Sineng SAU-100 (gateway for inverter 1) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 4 current
INVERTER_1.INV1_String_CURRENT_I5 |  | Sineng SAU-100 (gateway for inverter 1) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 5 current
INVERTER_1.INV1_String_CURRENT_I6 |  | Sineng SAU-100 (gateway for inverter 1) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 6 current
INVERTER_1.INV1_String_CURRENT_I7 |  | Sineng SAU-100 (gateway for inverter 1) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 7 current
INVERTER_1.INV1_String_CURRENT_I8 |  | Sineng SAU-100 (gateway for inverter 1) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 8 current
INVERTER_1.INV1_String_CURRENT_I9 |  | Sineng SAU-100 (gateway for inverter 1) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 9 current
INVERTER_1.INV1_String_CURRENT_I10 |  | Sineng SAU-100 (gateway for inverter 1) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 10 current
INVERTER_1.INV1_String_CURRENT_I11 |  | Sineng SAU-100 (gateway for inverter 1) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 11 current
INVERTER_1.INV1_String_CURRENT_I12 |  | Sineng SAU-100 (gateway for inverter 1) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 12 current
INVERTER_1.INV1_String_CURRENT_I13 |  | Sineng SAU-100 (gateway for inverter 1) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 13 current
INVERTER_1.INV1_String_CURRENT_I14 |  | Sineng SAU-100 (gateway for inverter 1) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 14 current
INVERTER_1.INV1_String_CURRENT_I15 |  | Sineng SAU-100 (gateway for inverter 1) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 15 current
INVERTER_1.INV1_String_CURRENT_I16 |  | Sineng SAU-100 (gateway for inverter 1) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 16 current
INVERTER_1.INV1_String_CURRENT_I17 |  | Sineng SAU-100 (gateway for inverter 1) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 17 current
INVERTER_1.INV1_TOTAL_PRODUCTION |  | Sineng SAU-100 (gateway for inverter 1) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | kWh | TBC | TBC | Lifetime energy
INVERTER_2.INV2_AC_POWER |  | Sineng SAU-100 (gateway for inverter 2) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | kW | TBC | TBC | Total active AC power
INVERTER_2.INV2_CURRENT_I1 |  | Sineng SAU-100 (gateway for inverter 2) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | AC phase current L1
INVERTER_2.INV2_CURRENT_I2 |  | Sineng SAU-100 (gateway for inverter 2) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | AC phase current L2
INVERTER_2.INV2_CURRENT_I3 |  | Sineng SAU-100 (gateway for inverter 2) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | AC phase current L3
INVERTER_2.INV2_DC_POWER |  | Sineng SAU-100 (gateway for inverter 2) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | kW | TBC | TBC | Total DC input power
INVERTER_2.INV2_FREKANS |  | Sineng SAU-100 (gateway for inverter 2) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | Hz | TBC | TBC | Grid frequency
INVERTER_2.INV2_VOLTAGE_V1 |  | Sineng SAU-100 (gateway for inverter 2) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | V | TBC | TBC | AC phase voltage L1
INVERTER_2.INV2_VOLTAGE_V2 |  | Sineng SAU-100 (gateway for inverter 2) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | V | TBC | TBC | AC phase voltage L2
INVERTER_2.INV2_VOLTAGE_V3 |  | Sineng SAU-100 (gateway for inverter 2) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | V | TBC | TBC | AC phase voltage L3
INVERTER_2.INV2_DAILY_PRODUCTION |  | Sineng SAU-100 (gateway for inverter 2) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | kWh | TBC | TBC | Energy today
INVERTER_2.INV2_Connection_Error |  | Sineng SAU-100 (gateway for inverter 2) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Boolean |  | TBC | TBC | 1 = inverter not responding on SAU RS485 bus
INVERTER_2.INV2_String_CURRENT_I1 |  | Sineng SAU-100 (gateway for inverter 2) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 1 current
INVERTER_2.INV2_String_CURRENT_I2 |  | Sineng SAU-100 (gateway for inverter 2) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 2 current
INVERTER_2.INV2_String_CURRENT_I3 |  | Sineng SAU-100 (gateway for inverter 2) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 3 current
INVERTER_2.INV2_String_CURRENT_I4 |  | Sineng SAU-100 (gateway for inverter 2) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 4 current
INVERTER_2.INV2_String_CURRENT_I5 |  | Sineng SAU-100 (gateway for inverter 2) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 5 current
INVERTER_2.INV2_String_CURRENT_I6 |  | Sineng SAU-100 (gateway for inverter 2) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 6 current
INVERTER_2.INV2_String_CURRENT_I7 |  | Sineng SAU-100 (gateway for inverter 2) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 7 current
INVERTER_2.INV2_String_CURRENT_I8 |  | Sineng SAU-100 (gateway for inverter 2) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 8 current
INVERTER_2.INV2_String_CURRENT_I9 |  | Sineng SAU-100 (gateway for inverter 2) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 9 current
INVERTER_2.INV2_String_CURRENT_I10 |  | Sineng SAU-100 (gateway for inverter 2) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 10 current
INVERTER_2.INV2_String_CURRENT_I11 |  | Sineng SAU-100 (gateway for inverter 2) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 11 current
INVERTER_2.INV2_String_CURRENT_I12 |  | Sineng SAU-100 (gateway for inverter 2) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 12 current
INVERTER_2.INV2_String_CURRENT_I13 |  | Sineng SAU-100 (gateway for inverter 2) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 13 current
INVERTER_2.INV2_String_CURRENT_I14 |  | Sineng SAU-100 (gateway for inverter 2) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 14 current
INVERTER_2.INV2_String_CURRENT_I15 |  | Sineng SAU-100 (gateway for inverter 2) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 15 current
INVERTER_2.INV2_String_CURRENT_I16 |  | Sineng SAU-100 (gateway for inverter 2) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 16 current
INVERTER_2.INV2_String_CURRENT_I17 |  | Sineng SAU-100 (gateway for inverter 2) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 17 current
INVERTER_2.INV2_TOTAL_PRODUCTION |  | Sineng SAU-100 (gateway for inverter 2) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | kWh | TBC | TBC | Lifetime energy
INVERTER_3.INV3_AC_POWER |  | Sineng SAU-100 (gateway for inverter 3) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | kW | TBC | TBC | Total active AC power
INVERTER_3.INV3_CURRENT_I1 |  | Sineng SAU-100 (gateway for inverter 3) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | AC phase current L1
INVERTER_3.INV3_CURRENT_I2 |  | Sineng SAU-100 (gateway for inverter 3) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | AC phase current L2
INVERTER_3.INV3_CURRENT_I3 |  | Sineng SAU-100 (gateway for inverter 3) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | AC phase current L3
INVERTER_3.INV3_DC_POWER |  | Sineng SAU-100 (gateway for inverter 3) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | kW | TBC | TBC | Total DC input power
INVERTER_3.INV3_FREKANS |  | Sineng SAU-100 (gateway for inverter 3) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | Hz | TBC | TBC | Grid frequency
INVERTER_3.INV3_VOLTAGE_V1 |  | Sineng SAU-100 (gateway for inverter 3) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | V | TBC | TBC | AC phase voltage L1
INVERTER_3.INV3_VOLTAGE_V2 |  | Sineng SAU-100 (gateway for inverter 3) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | V | TBC | TBC | AC phase voltage L2
INVERTER_3.INV3_VOLTAGE_V3 |  | Sineng SAU-100 (gateway for inverter 3) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | V | TBC | TBC | AC phase voltage L3
INVERTER_3.INV3_DAILY_PRODUCTION |  | Sineng SAU-100 (gateway for inverter 3) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | kWh | TBC | TBC | Energy today
INVERTER_3.INV3_Connection_Error |  | Sineng SAU-100 (gateway for inverter 3) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Boolean |  | TBC | TBC | 1 = inverter not responding on SAU RS485 bus
INVERTER_3.INV3_String_CURRENT_I1 |  | Sineng SAU-100 (gateway for inverter 3) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 1 current
INVERTER_3.INV3_String_CURRENT_I2 |  | Sineng SAU-100 (gateway for inverter 3) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 2 current
INVERTER_3.INV3_String_CURRENT_I3 |  | Sineng SAU-100 (gateway for inverter 3) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 3 current
INVERTER_3.INV3_String_CURRENT_I4 |  | Sineng SAU-100 (gateway for inverter 3) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 4 current
INVERTER_3.INV3_String_CURRENT_I5 |  | Sineng SAU-100 (gateway for inverter 3) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 5 current
INVERTER_3.INV3_String_CURRENT_I6 |  | Sineng SAU-100 (gateway for inverter 3) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 6 current
INVERTER_3.INV3_String_CURRENT_I7 |  | Sineng SAU-100 (gateway for inverter 3) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 7 current
INVERTER_3.INV3_String_CURRENT_I8 |  | Sineng SAU-100 (gateway for inverter 3) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 8 current
INVERTER_3.INV3_String_CURRENT_I9 |  | Sineng SAU-100 (gateway for inverter 3) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 9 current
INVERTER_3.INV3_String_CURRENT_I10 |  | Sineng SAU-100 (gateway for inverter 3) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 10 current
INVERTER_3.INV3_String_CURRENT_I11 |  | Sineng SAU-100 (gateway for inverter 3) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 11 current
INVERTER_3.INV3_String_CURRENT_I12 |  | Sineng SAU-100 (gateway for inverter 3) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 12 current
INVERTER_3.INV3_String_CURRENT_I13 |  | Sineng SAU-100 (gateway for inverter 3) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 13 current
INVERTER_3.INV3_String_CURRENT_I14 |  | Sineng SAU-100 (gateway for inverter 3) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 14 current
INVERTER_3.INV3_String_CURRENT_I15 |  | Sineng SAU-100 (gateway for inverter 3) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 15 current
INVERTER_3.INV3_String_CURRENT_I16 |  | Sineng SAU-100 (gateway for inverter 3) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 16 current
INVERTER_3.INV3_String_CURRENT_I17 |  | Sineng SAU-100 (gateway for inverter 3) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 17 current
INVERTER_3.INV3_TOTAL_PRODUCTION |  | Sineng SAU-100 (gateway for inverter 3) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | kWh | TBC | TBC | Lifetime energy
INVERTER_4.INV4_AC_POWER |  | Sineng SAU-100 (gateway for inverter 4) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | kW | TBC | TBC | Total active AC power
INVERTER_4.INV4_CURRENT_I1 |  | Sineng SAU-100 (gateway for inverter 4) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | AC phase current L1
INVERTER_4.INV4_CURRENT_I2 |  | Sineng SAU-100 (gateway for inverter 4) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | AC phase current L2
INVERTER_4.INV4_CURRENT_I3 |  | Sineng SAU-100 (gateway for inverter 4) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | AC phase current L3
INVERTER_4.INV4_DC_POWER |  | Sineng SAU-100 (gateway for inverter 4) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | kW | TBC | TBC | Total DC input power
INVERTER_4.INV4_FREKANS |  | Sineng SAU-100 (gateway for inverter 4) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | Hz | TBC | TBC | Grid frequency
INVERTER_4.INV4_VOLTAGE_V1 |  | Sineng SAU-100 (gateway for inverter 4) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | V | TBC | TBC | AC phase voltage L1
INVERTER_4.INV4_VOLTAGE_V2 |  | Sineng SAU-100 (gateway for inverter 4) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | V | TBC | TBC | AC phase voltage L2
INVERTER_4.INV4_VOLTAGE_V3 |  | Sineng SAU-100 (gateway for inverter 4) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | V | TBC | TBC | AC phase voltage L3
INVERTER_4.INV4_DAILY_PRODUCTION |  | Sineng SAU-100 (gateway for inverter 4) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | kWh | TBC | TBC | Energy today
INVERTER_4.INV4_Connection_Error |  | Sineng SAU-100 (gateway for inverter 4) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Boolean |  | TBC | TBC | 1 = inverter not responding on SAU RS485 bus
INVERTER_4.INV4_String_CURRENT_I1 |  | Sineng SAU-100 (gateway for inverter 4) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 1 current
INVERTER_4.INV4_String_CURRENT_I2 |  | Sineng SAU-100 (gateway for inverter 4) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 2 current
INVERTER_4.INV4_String_CURRENT_I3 |  | Sineng SAU-100 (gateway for inverter 4) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 3 current
INVERTER_4.INV4_String_CURRENT_I4 |  | Sineng SAU-100 (gateway for inverter 4) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 4 current
INVERTER_4.INV4_String_CURRENT_I5 |  | Sineng SAU-100 (gateway for inverter 4) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 5 current
INVERTER_4.INV4_String_CURRENT_I6 |  | Sineng SAU-100 (gateway for inverter 4) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 6 current
INVERTER_4.INV4_String_CURRENT_I7 |  | Sineng SAU-100 (gateway for inverter 4) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 7 current
INVERTER_4.INV4_String_CURRENT_I8 |  | Sineng SAU-100 (gateway for inverter 4) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 8 current
INVERTER_4.INV4_String_CURRENT_I9 |  | Sineng SAU-100 (gateway for inverter 4) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 9 current
INVERTER_4.INV4_String_CURRENT_I10 |  | Sineng SAU-100 (gateway for inverter 4) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 10 current
INVERTER_4.INV4_String_CURRENT_I11 |  | Sineng SAU-100 (gateway for inverter 4) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 11 current
INVERTER_4.INV4_String_CURRENT_I12 |  | Sineng SAU-100 (gateway for inverter 4) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 12 current
INVERTER_4.INV4_String_CURRENT_I13 |  | Sineng SAU-100 (gateway for inverter 4) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 13 current
INVERTER_4.INV4_String_CURRENT_I14 |  | Sineng SAU-100 (gateway for inverter 4) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 14 current
INVERTER_4.INV4_String_CURRENT_I15 |  | Sineng SAU-100 (gateway for inverter 4) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 15 current
INVERTER_4.INV4_String_CURRENT_I16 |  | Sineng SAU-100 (gateway for inverter 4) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 16 current
INVERTER_4.INV4_String_CURRENT_I17 |  | Sineng SAU-100 (gateway for inverter 4) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 17 current
INVERTER_4.INV4_TOTAL_PRODUCTION |  | Sineng SAU-100 (gateway for inverter 4) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | kWh | TBC | TBC | Lifetime energy
INVERTER_5.INV5_AC_POWER |  | Sineng SAU-100 (gateway for inverter 5) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | kW | TBC | TBC | Total active AC power
INVERTER_5.INV5_CURRENT_I1 |  | Sineng SAU-100 (gateway for inverter 5) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | AC phase current L1
INVERTER_5.INV5_CURRENT_I2 |  | Sineng SAU-100 (gateway for inverter 5) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | AC phase current L2
INVERTER_5.INV5_CURRENT_I3 |  | Sineng SAU-100 (gateway for inverter 5) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | AC phase current L3
INVERTER_5.INV5_DC_POWER |  | Sineng SAU-100 (gateway for inverter 5) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | kW | TBC | TBC | Total DC input power
INVERTER_5.INV5_FREKANS |  | Sineng SAU-100 (gateway for inverter 5) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | Hz | TBC | TBC | Grid frequency
INVERTER_5.INV5_VOLTAGE_V1 |  | Sineng SAU-100 (gateway for inverter 5) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | V | TBC | TBC | AC phase voltage L1
INVERTER_5.INV5_VOLTAGE_V2 |  | Sineng SAU-100 (gateway for inverter 5) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | V | TBC | TBC | AC phase voltage L2
INVERTER_5.INV5_VOLTAGE_V3 |  | Sineng SAU-100 (gateway for inverter 5) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | V | TBC | TBC | AC phase voltage L3
INVERTER_5.INV5_DAILY_PRODUCTION |  | Sineng SAU-100 (gateway for inverter 5) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | kWh | TBC | TBC | Energy today
INVERTER_5.INV5_Connection_Error |  | Sineng SAU-100 (gateway for inverter 5) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Boolean |  | TBC | TBC | 1 = inverter not responding on SAU RS485 bus
INVERTER_5.INV5_String_CURRENT_I1 |  | Sineng SAU-100 (gateway for inverter 5) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 1 current
INVERTER_5.INV5_String_CURRENT_I2 |  | Sineng SAU-100 (gateway for inverter 5) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 2 current
INVERTER_5.INV5_String_CURRENT_I3 |  | Sineng SAU-100 (gateway for inverter 5) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 3 current
INVERTER_5.INV5_String_CURRENT_I4 |  | Sineng SAU-100 (gateway for inverter 5) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 4 current
INVERTER_5.INV5_String_CURRENT_I5 |  | Sineng SAU-100 (gateway for inverter 5) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 5 current
INVERTER_5.INV5_String_CURRENT_I6 |  | Sineng SAU-100 (gateway for inverter 5) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 6 current
INVERTER_5.INV5_String_CURRENT_I7 |  | Sineng SAU-100 (gateway for inverter 5) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 7 current
INVERTER_5.INV5_String_CURRENT_I8 |  | Sineng SAU-100 (gateway for inverter 5) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 8 current
INVERTER_5.INV5_String_CURRENT_I9 |  | Sineng SAU-100 (gateway for inverter 5) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 9 current
INVERTER_5.INV5_String_CURRENT_I10 |  | Sineng SAU-100 (gateway for inverter 5) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 10 current
INVERTER_5.INV5_String_CURRENT_I11 |  | Sineng SAU-100 (gateway for inverter 5) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 11 current
INVERTER_5.INV5_String_CURRENT_I12 |  | Sineng SAU-100 (gateway for inverter 5) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 12 current
INVERTER_5.INV5_String_CURRENT_I13 |  | Sineng SAU-100 (gateway for inverter 5) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 13 current
INVERTER_5.INV5_String_CURRENT_I14 |  | Sineng SAU-100 (gateway for inverter 5) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 14 current
INVERTER_5.INV5_String_CURRENT_I15 |  | Sineng SAU-100 (gateway for inverter 5) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 15 current
INVERTER_5.INV5_String_CURRENT_I16 |  | Sineng SAU-100 (gateway for inverter 5) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 16 current
INVERTER_5.INV5_String_CURRENT_I17 |  | Sineng SAU-100 (gateway for inverter 5) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 17 current
INVERTER_5.INV5_TOTAL_PRODUCTION |  | Sineng SAU-100 (gateway for inverter 5) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | kWh | TBC | TBC | Lifetime energy
INVERTER_6.INV6_AC_POWER |  | Sineng SAU-100 (gateway for inverter 6) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | kW | TBC | TBC | Total active AC power
INVERTER_6.INV6_CURRENT_I1 |  | Sineng SAU-100 (gateway for inverter 6) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | AC phase current L1
INVERTER_6.INV6_CURRENT_I2 |  | Sineng SAU-100 (gateway for inverter 6) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | AC phase current L2
INVERTER_6.INV6_CURRENT_I3 |  | Sineng SAU-100 (gateway for inverter 6) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | AC phase current L3
INVERTER_6.INV6_DC_POWER |  | Sineng SAU-100 (gateway for inverter 6) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | kW | TBC | TBC | Total DC input power
INVERTER_6.INV6_FREKANS |  | Sineng SAU-100 (gateway for inverter 6) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | Hz | TBC | TBC | Grid frequency
INVERTER_6.INV6_VOLTAGE_V1 |  | Sineng SAU-100 (gateway for inverter 6) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | V | TBC | TBC | AC phase voltage L1
INVERTER_6.INV6_VOLTAGE_V2 |  | Sineng SAU-100 (gateway for inverter 6) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | V | TBC | TBC | AC phase voltage L2
INVERTER_6.INV6_VOLTAGE_V3 |  | Sineng SAU-100 (gateway for inverter 6) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | V | TBC | TBC | AC phase voltage L3
INVERTER_6.INV6_DAILY_PRODUCTION |  | Sineng SAU-100 (gateway for inverter 6) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | kWh | TBC | TBC | Energy today
INVERTER_6.INV6_Connection_Error |  | Sineng SAU-100 (gateway for inverter 6) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Boolean |  | TBC | TBC | 1 = inverter not responding on SAU RS485 bus
INVERTER_6.INV6_String_CURRENT_I1 |  | Sineng SAU-100 (gateway for inverter 6) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 1 current
INVERTER_6.INV6_String_CURRENT_I2 |  | Sineng SAU-100 (gateway for inverter 6) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 2 current
INVERTER_6.INV6_String_CURRENT_I3 |  | Sineng SAU-100 (gateway for inverter 6) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 3 current
INVERTER_6.INV6_String_CURRENT_I4 |  | Sineng SAU-100 (gateway for inverter 6) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 4 current
INVERTER_6.INV6_String_CURRENT_I5 |  | Sineng SAU-100 (gateway for inverter 6) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 5 current
INVERTER_6.INV6_String_CURRENT_I6 |  | Sineng SAU-100 (gateway for inverter 6) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 6 current
INVERTER_6.INV6_String_CURRENT_I7 |  | Sineng SAU-100 (gateway for inverter 6) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 7 current
INVERTER_6.INV6_String_CURRENT_I8 |  | Sineng SAU-100 (gateway for inverter 6) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 8 current
INVERTER_6.INV6_String_CURRENT_I9 |  | Sineng SAU-100 (gateway for inverter 6) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 9 current
INVERTER_6.INV6_String_CURRENT_I10 |  | Sineng SAU-100 (gateway for inverter 6) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 10 current
INVERTER_6.INV6_String_CURRENT_I11 |  | Sineng SAU-100 (gateway for inverter 6) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 11 current
INVERTER_6.INV6_String_CURRENT_I12 |  | Sineng SAU-100 (gateway for inverter 6) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 12 current
INVERTER_6.INV6_String_CURRENT_I13 |  | Sineng SAU-100 (gateway for inverter 6) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 13 current
INVERTER_6.INV6_String_CURRENT_I14 |  | Sineng SAU-100 (gateway for inverter 6) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 14 current
INVERTER_6.INV6_String_CURRENT_I15 |  | Sineng SAU-100 (gateway for inverter 6) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 15 current
INVERTER_6.INV6_String_CURRENT_I16 |  | Sineng SAU-100 (gateway for inverter 6) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 16 current
INVERTER_6.INV6_String_CURRENT_I17 |  | Sineng SAU-100 (gateway for inverter 6) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 17 current
INVERTER_6.INV6_TOTAL_PRODUCTION |  | Sineng SAU-100 (gateway for inverter 6) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | kWh | TBC | TBC | Lifetime energy
INVERTER_7.INV7_AC_POWER |  | Sineng SAU-100 (gateway for inverter 7) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | kW | TBC | TBC | Total active AC power
INVERTER_7.INV7_CURRENT_I1 |  | Sineng SAU-100 (gateway for inverter 7) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | AC phase current L1
INVERTER_7.INV7_CURRENT_I2 |  | Sineng SAU-100 (gateway for inverter 7) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | AC phase current L2
INVERTER_7.INV7_CURRENT_I3 |  | Sineng SAU-100 (gateway for inverter 7) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | AC phase current L3
INVERTER_7.INV7_DC_POWER |  | Sineng SAU-100 (gateway for inverter 7) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | kW | TBC | TBC | Total DC input power
INVERTER_7.INV7_FREKANS |  | Sineng SAU-100 (gateway for inverter 7) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | Hz | TBC | TBC | Grid frequency
INVERTER_7.INV7_VOLTAGE_V1 |  | Sineng SAU-100 (gateway for inverter 7) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | V | TBC | TBC | AC phase voltage L1
INVERTER_7.INV7_VOLTAGE_V2 |  | Sineng SAU-100 (gateway for inverter 7) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | V | TBC | TBC | AC phase voltage L2
INVERTER_7.INV7_VOLTAGE_V3 |  | Sineng SAU-100 (gateway for inverter 7) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | V | TBC | TBC | AC phase voltage L3
INVERTER_7.INV7_DAILY_PRODUCTION |  | Sineng SAU-100 (gateway for inverter 7) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | kWh | TBC | TBC | Energy today
INVERTER_7.INV7_Connection_Error |  | Sineng SAU-100 (gateway for inverter 7) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Boolean |  | TBC | TBC | 1 = inverter not responding on SAU RS485 bus
INVERTER_7.INV7_String_CURRENT_I1 |  | Sineng SAU-100 (gateway for inverter 7) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 1 current
INVERTER_7.INV7_String_CURRENT_I2 |  | Sineng SAU-100 (gateway for inverter 7) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 2 current
INVERTER_7.INV7_String_CURRENT_I3 |  | Sineng SAU-100 (gateway for inverter 7) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 3 current
INVERTER_7.INV7_String_CURRENT_I4 |  | Sineng SAU-100 (gateway for inverter 7) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 4 current
INVERTER_7.INV7_String_CURRENT_I5 |  | Sineng SAU-100 (gateway for inverter 7) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 5 current
INVERTER_7.INV7_String_CURRENT_I6 |  | Sineng SAU-100 (gateway for inverter 7) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 6 current
INVERTER_7.INV7_String_CURRENT_I7 |  | Sineng SAU-100 (gateway for inverter 7) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 7 current
INVERTER_7.INV7_String_CURRENT_I8 |  | Sineng SAU-100 (gateway for inverter 7) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 8 current
INVERTER_7.INV7_String_CURRENT_I9 |  | Sineng SAU-100 (gateway for inverter 7) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 9 current
INVERTER_7.INV7_String_CURRENT_I10 |  | Sineng SAU-100 (gateway for inverter 7) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 10 current
INVERTER_7.INV7_String_CURRENT_I11 |  | Sineng SAU-100 (gateway for inverter 7) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 11 current
INVERTER_7.INV7_String_CURRENT_I12 |  | Sineng SAU-100 (gateway for inverter 7) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 12 current
INVERTER_7.INV7_String_CURRENT_I13 |  | Sineng SAU-100 (gateway for inverter 7) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 13 current
INVERTER_7.INV7_String_CURRENT_I14 |  | Sineng SAU-100 (gateway for inverter 7) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 14 current
INVERTER_7.INV7_String_CURRENT_I15 |  | Sineng SAU-100 (gateway for inverter 7) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 15 current
INVERTER_7.INV7_String_CURRENT_I16 |  | Sineng SAU-100 (gateway for inverter 7) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 16 current
INVERTER_7.INV7_String_CURRENT_I17 |  | Sineng SAU-100 (gateway for inverter 7) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 17 current
INVERTER_7.INV7_TOTAL_PRODUCTION |  | Sineng SAU-100 (gateway for inverter 7) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | kWh | TBC | TBC | Lifetime energy
INVERTER_8.INV8_AC_POWER |  | Sineng SAU-100 (gateway for inverter 8) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | kW | TBC | TBC | Total active AC power
INVERTER_8.INV8_CURRENT_I1 |  | Sineng SAU-100 (gateway for inverter 8) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | AC phase current L1
INVERTER_8.INV8_CURRENT_I2 |  | Sineng SAU-100 (gateway for inverter 8) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | AC phase current L2
INVERTER_8.INV8_CURRENT_I3 |  | Sineng SAU-100 (gateway for inverter 8) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | AC phase current L3
INVERTER_8.INV8_DC_POWER |  | Sineng SAU-100 (gateway for inverter 8) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | kW | TBC | TBC | Total DC input power
INVERTER_8.INV8_FREKANS |  | Sineng SAU-100 (gateway for inverter 8) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | Hz | TBC | TBC | Grid frequency
INVERTER_8.INV8_VOLTAGE_V1 |  | Sineng SAU-100 (gateway for inverter 8) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | V | TBC | TBC | AC phase voltage L1
INVERTER_8.INV8_VOLTAGE_V2 |  | Sineng SAU-100 (gateway for inverter 8) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | V | TBC | TBC | AC phase voltage L2
INVERTER_8.INV8_VOLTAGE_V3 |  | Sineng SAU-100 (gateway for inverter 8) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | V | TBC | TBC | AC phase voltage L3
INVERTER_8.INV8_DAILY_PRODUCTION |  | Sineng SAU-100 (gateway for inverter 8) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | kWh | TBC | TBC | Energy today
INVERTER_8.INV8_Connection_Error |  | Sineng SAU-100 (gateway for inverter 8) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Boolean |  | TBC | TBC | 1 = inverter not responding on SAU RS485 bus
INVERTER_8.INV8_String_CURRENT_I1 |  | Sineng SAU-100 (gateway for inverter 8) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 1 current
INVERTER_8.INV8_String_CURRENT_I2 |  | Sineng SAU-100 (gateway for inverter 8) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 2 current
INVERTER_8.INV8_String_CURRENT_I3 |  | Sineng SAU-100 (gateway for inverter 8) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 3 current
INVERTER_8.INV8_String_CURRENT_I4 |  | Sineng SAU-100 (gateway for inverter 8) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 4 current
INVERTER_8.INV8_String_CURRENT_I5 |  | Sineng SAU-100 (gateway for inverter 8) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 5 current
INVERTER_8.INV8_String_CURRENT_I6 |  | Sineng SAU-100 (gateway for inverter 8) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 6 current
INVERTER_8.INV8_String_CURRENT_I7 |  | Sineng SAU-100 (gateway for inverter 8) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 7 current
INVERTER_8.INV8_String_CURRENT_I8 |  | Sineng SAU-100 (gateway for inverter 8) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 8 current
INVERTER_8.INV8_String_CURRENT_I9 |  | Sineng SAU-100 (gateway for inverter 8) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 9 current
INVERTER_8.INV8_String_CURRENT_I10 |  | Sineng SAU-100 (gateway for inverter 8) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 10 current
INVERTER_8.INV8_String_CURRENT_I11 |  | Sineng SAU-100 (gateway for inverter 8) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 11 current
INVERTER_8.INV8_String_CURRENT_I12 |  | Sineng SAU-100 (gateway for inverter 8) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 12 current
INVERTER_8.INV8_String_CURRENT_I13 |  | Sineng SAU-100 (gateway for inverter 8) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 13 current
INVERTER_8.INV8_String_CURRENT_I14 |  | Sineng SAU-100 (gateway for inverter 8) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 14 current
INVERTER_8.INV8_String_CURRENT_I15 |  | Sineng SAU-100 (gateway for inverter 8) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 15 current
INVERTER_8.INV8_String_CURRENT_I16 |  | Sineng SAU-100 (gateway for inverter 8) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 16 current
INVERTER_8.INV8_String_CURRENT_I17 |  | Sineng SAU-100 (gateway for inverter 8) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 17 current
INVERTER_8.INV8_TOTAL_PRODUCTION |  | Sineng SAU-100 (gateway for inverter 8) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | kWh | TBC | TBC | Lifetime energy
INVERTER_9.INV9_AC_POWER |  | Sineng SAU-100 (gateway for inverter 9) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | kW | TBC | TBC | Total active AC power
INVERTER_9.INV9_CURRENT_I1 |  | Sineng SAU-100 (gateway for inverter 9) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | AC phase current L1
INVERTER_9.INV9_CURRENT_I2 |  | Sineng SAU-100 (gateway for inverter 9) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | AC phase current L2
INVERTER_9.INV9_CURRENT_I3 |  | Sineng SAU-100 (gateway for inverter 9) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | AC phase current L3
INVERTER_9.INV9_DC_POWER |  | Sineng SAU-100 (gateway for inverter 9) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | kW | TBC | TBC | Total DC input power
INVERTER_9.INV9_FREKANS |  | Sineng SAU-100 (gateway for inverter 9) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | Hz | TBC | TBC | Grid frequency
INVERTER_9.INV9_VOLTAGE_V1 |  | Sineng SAU-100 (gateway for inverter 9) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | V | TBC | TBC | AC phase voltage L1
INVERTER_9.INV9_VOLTAGE_V2 |  | Sineng SAU-100 (gateway for inverter 9) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | V | TBC | TBC | AC phase voltage L2
INVERTER_9.INV9_VOLTAGE_V3 |  | Sineng SAU-100 (gateway for inverter 9) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | V | TBC | TBC | AC phase voltage L3
INVERTER_9.INV9_DAILY_PRODUCTION |  | Sineng SAU-100 (gateway for inverter 9) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | kWh | TBC | TBC | Energy today
INVERTER_9.INV9_Connection_Error |  | Sineng SAU-100 (gateway for inverter 9) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Boolean |  | TBC | TBC | 1 = inverter not responding on SAU RS485 bus
INVERTER_9.INV9_String_CURRENT_I1 |  | Sineng SAU-100 (gateway for inverter 9) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 1 current
INVERTER_9.INV9_String_CURRENT_I2 |  | Sineng SAU-100 (gateway for inverter 9) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 2 current
INVERTER_9.INV9_String_CURRENT_I3 |  | Sineng SAU-100 (gateway for inverter 9) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 3 current
INVERTER_9.INV9_String_CURRENT_I4 |  | Sineng SAU-100 (gateway for inverter 9) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 4 current
INVERTER_9.INV9_String_CURRENT_I5 |  | Sineng SAU-100 (gateway for inverter 9) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 5 current
INVERTER_9.INV9_String_CURRENT_I6 |  | Sineng SAU-100 (gateway for inverter 9) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 6 current
INVERTER_9.INV9_String_CURRENT_I7 |  | Sineng SAU-100 (gateway for inverter 9) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 7 current
INVERTER_9.INV9_String_CURRENT_I8 |  | Sineng SAU-100 (gateway for inverter 9) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 8 current
INVERTER_9.INV9_String_CURRENT_I9 |  | Sineng SAU-100 (gateway for inverter 9) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 9 current
INVERTER_9.INV9_String_CURRENT_I10 |  | Sineng SAU-100 (gateway for inverter 9) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 10 current
INVERTER_9.INV9_String_CURRENT_I11 |  | Sineng SAU-100 (gateway for inverter 9) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 11 current
INVERTER_9.INV9_String_CURRENT_I12 |  | Sineng SAU-100 (gateway for inverter 9) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 12 current
INVERTER_9.INV9_String_CURRENT_I13 |  | Sineng SAU-100 (gateway for inverter 9) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 13 current
INVERTER_9.INV9_String_CURRENT_I14 |  | Sineng SAU-100 (gateway for inverter 9) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 14 current
INVERTER_9.INV9_String_CURRENT_I15 |  | Sineng SAU-100 (gateway for inverter 9) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 15 current
INVERTER_9.INV9_String_CURRENT_I16 |  | Sineng SAU-100 (gateway for inverter 9) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 16 current
INVERTER_9.INV9_String_CURRENT_I17 |  | Sineng SAU-100 (gateway for inverter 9) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 17 current
INVERTER_9.INV9_TOTAL_PRODUCTION |  | Sineng SAU-100 (gateway for inverter 9) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | kWh | TBC | TBC | Lifetime energy
INVERTER_10.INV10_AC_POWER |  | Sineng SAU-100 (gateway for inverter 10) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | kW | TBC | TBC | Total active AC power
INVERTER_10.INV10_CURRENT_I1 |  | Sineng SAU-100 (gateway for inverter 10) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | AC phase current L1
INVERTER_10.INV10_CURRENT_I2 |  | Sineng SAU-100 (gateway for inverter 10) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | AC phase current L2
INVERTER_10.INV10_CURRENT_I3 |  | Sineng SAU-100 (gateway for inverter 10) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | AC phase current L3
INVERTER_10.INV10_DC_POWER |  | Sineng SAU-100 (gateway for inverter 10) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | kW | TBC | TBC | Total DC input power
INVERTER_10.INV10_FREKANS |  | Sineng SAU-100 (gateway for inverter 10) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | Hz | TBC | TBC | Grid frequency
INVERTER_10.INV10_VOLTAGE_V1 |  | Sineng SAU-100 (gateway for inverter 10) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | V | TBC | TBC | AC phase voltage L1
INVERTER_10.INV10_VOLTAGE_V2 |  | Sineng SAU-100 (gateway for inverter 10) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | V | TBC | TBC | AC phase voltage L2
INVERTER_10.INV10_VOLTAGE_V3 |  | Sineng SAU-100 (gateway for inverter 10) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | V | TBC | TBC | AC phase voltage L3
INVERTER_10.INV10_DAILY_PRODUCTION |  | Sineng SAU-100 (gateway for inverter 10) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | kWh | TBC | TBC | Energy today
INVERTER_10.INV10_Connection_Error |  | Sineng SAU-100 (gateway for inverter 10) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Boolean |  | TBC | TBC | 1 = inverter not responding on SAU RS485 bus
INVERTER_10.INV10_String_CURRENT_I1 |  | Sineng SAU-100 (gateway for inverter 10) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 1 current
INVERTER_10.INV10_String_CURRENT_I2 |  | Sineng SAU-100 (gateway for inverter 10) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 2 current
INVERTER_10.INV10_String_CURRENT_I3 |  | Sineng SAU-100 (gateway for inverter 10) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 3 current
INVERTER_10.INV10_String_CURRENT_I4 |  | Sineng SAU-100 (gateway for inverter 10) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 4 current
INVERTER_10.INV10_String_CURRENT_I5 |  | Sineng SAU-100 (gateway for inverter 10) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 5 current
INVERTER_10.INV10_String_CURRENT_I6 |  | Sineng SAU-100 (gateway for inverter 10) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 6 current
INVERTER_10.INV10_String_CURRENT_I7 |  | Sineng SAU-100 (gateway for inverter 10) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 7 current
INVERTER_10.INV10_String_CURRENT_I8 |  | Sineng SAU-100 (gateway for inverter 10) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 8 current
INVERTER_10.INV10_String_CURRENT_I9 |  | Sineng SAU-100 (gateway for inverter 10) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 9 current
INVERTER_10.INV10_String_CURRENT_I10 |  | Sineng SAU-100 (gateway for inverter 10) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 10 current
INVERTER_10.INV10_String_CURRENT_I11 |  | Sineng SAU-100 (gateway for inverter 10) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 11 current
INVERTER_10.INV10_String_CURRENT_I12 |  | Sineng SAU-100 (gateway for inverter 10) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 12 current
INVERTER_10.INV10_String_CURRENT_I13 |  | Sineng SAU-100 (gateway for inverter 10) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 13 current
INVERTER_10.INV10_String_CURRENT_I14 |  | Sineng SAU-100 (gateway for inverter 10) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 14 current
INVERTER_10.INV10_String_CURRENT_I15 |  | Sineng SAU-100 (gateway for inverter 10) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 15 current
INVERTER_10.INV10_String_CURRENT_I16 |  | Sineng SAU-100 (gateway for inverter 10) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 16 current
INVERTER_10.INV10_String_CURRENT_I17 |  | Sineng SAU-100 (gateway for inverter 10) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | A | TBC | TBC | DC string 17 current
INVERTER_10.INV10_TOTAL_PRODUCTION |  | Sineng SAU-100 (gateway for inverter 10) | Modbus TCP | 192.168.0.128:502 |  | Holding (FC03) — TBC | Float | kWh | TBC | TBC | Lifetime energy

## INFO
Item | Value / status
Site | Coca-Cola plant, Erbil — hybrid microgrid (grid + 5 gensets + PV)
Solar system vendor | Sineng Electric (inverters) — inverter model: TBC from nameplate
Number of inverters | 10 string inverters (template extended from 8 to 10)
PV gateway / logger | Sineng SAU-100, IP 192.168.0.128 (plant LAN), second interface 192.168.1.123; web UI http://192.168.0.128
Inverter ↔ SAU link | RS485 (Modbus RTU) from inverters to SAU, two groups; SAU exposes all inverters as Modbus TCP server on port 502
Other devices on SAU | Electric meter(s) and PID device(s) configured in SAU (seen in SAU device list) — details TBC
Existing monitoring | SAU local web UI (Device Monitor); ComAp InteliNeo 5500 master controller (IP 192.168.0.112) reads PV as 'PV Logger group 1/2' via Modbus TCP, unit address 245; plant SCADA PC; no cloud platform confirmed
ComAp data source | InteliNeo 5500 — Modbus TCP server; register list to be exported from InteliConfig (Modules → Modbus Registers). Gensets: 5 ComAp genset controllers; grid: 3 InteliMains 210
Protocols available | Modbus TCP (SAU, InteliNeo); Modbus RTU (inverters ↔ SAU, RS485); ComAp AirGate/WebSupervisor possible for InteliNeo (not enabled yet)
Data access status | Local LAN only today. The SAU Modbus server is already at its limit (send-queue congestion, comm-fail events in InteliNeo history, Oct 2026). ANY NEW POLLING OF THE SAU OR INTELINEO MUST BE COORDINATED — see NOTES
Documentation available | InteliNeo history exports, SAU diagnostics screenshots, integrator site-visit report (Stromatik, 28.09.2026). Still needed: Sineng inverter Modbus map, SAU point table, InteliConfig register export, single-line diagram
Technical contacts | Eng. Yousif (site); Sabir (data / monitoring integration); Stromatik Automation, Eng. Salwan (ComAp integrator); Sineng support (via site)
Revision | Rev.1.2 — structure and known values completed; register addresses marked TBC pending SAU point table and InteliConfig export

## NOTES
How to read this file
Yellow cells = value still to be confirmed (TBC). Green cells = confirmed from the site.
PLC_Address / Register = Modbus register on the source device. Convention: Modbus TCP, holding registers (FC03) unless stated; address as listed in the vendor point table (state 0-based or 1-based in Notes when known).
Where the missing addresses come from
1. Inverter signals: the Sineng SAU-100 web UI exports the Modbus point table for the connected inverters (Setting → communication / point table). Alternatively the Sineng inverter Modbus protocol document for the installed model. Unit ID per inverter = the inverter's address on the SAU.
2. Plant-level electrical signals (currents, voltages, P, Q, energy): from the electric meter connected to the SAU, or from the InteliNeo 5500 PV/bus measurements — whichever the site confirms as the official metering point.
3. Panel temperature / pyranometer: environmental sensors — confirm whether they are wired to the SAU (weather station input) or to another device.
4. Breaker states (LV panel thermal-magnetic switch): PVCB status as seen by the InteliNeo (binary input) — register from the InteliConfig Modbus register export.
5. ComAp values (PV prod, PV req, bus values, comm status): InteliConfig → Modules → Modbus Registers export of the InteliNeo configuration.
IMPORTANT for the monitoring integration
The SAU Modbus TCP server is single-threaded and is already overloaded by the InteliNeo polling (two sessions, 0 ms pause). Comm-fail events in the InteliNeo cause PV anti-islanding trips and bus under-voltage. Adding another Modbus client directly on the SAU or the InteliNeo will make this worse.
Recommended architecture: ONE local data collector on site reads the SAU and the InteliNeo gently (or reads the SCADA historian) and serves all consumers (DT Turkey monitoring, local dashboards) from its own database/OPC-UA/REST. No second poller on the field devices.
The 290 inverter tags (10 inverters × 29 signals) should be read in block reads per inverter, at ≥ 10 s interval, not tag-by-tag.