## SOLAR_Tag_list
Tag Name | PLC Address | Data Type | Description | Source Device | Protocol | IP:Port | Unit ID | Register / FC | Unit | Scale | Status | Notes
Apparent current L1 N |  | Float |  | SAU-100 electric meter (LV PV panel) | Modbus TCP | 192.168.0.128:502 | TBC (meter address on SAU) | TBC | A | TBC | TBC | Confirm official metering point: SAU meter or InteliNeo PV measurement
Apparent current L2 N |  | Float | Apparent current L2 N | SAU-100 electric meter (LV PV panel) | Modbus TCP | 192.168.0.128:502 | TBC (meter address on SAU) | TBC | A | TBC | TBC
Apparent current L3 N |  | Float |  | SAU-100 electric meter (LV PV panel) | Modbus TCP | 192.168.0.128:502 | TBC (meter address on SAU) | TBC | A | TBC | TBC
Psum3 |  | Float | Psum3=P1+P2+P3 | SAU-100 electric meter (LV PV panel) | Modbus TCP | 192.168.0.128:502 | TBC (meter address on SAU) | TBC | kW | TBC | TBC | Also available in InteliNeo as 'PV prod' (sum of both logger groups)
Qsum3 |  | Float | Qsum3=Q1+Q2+Q3 (fundamental comp ) | SAU-100 electric meter (LV PV panel) | Modbus TCP | 192.168.0.128:502 | TBC (meter address on SAU) | TBC | kvar | TBC | TBC
Real energy L1 L3 delivered |  | Float |  | SAU-100 electric meter (LV PV panel) | Modbus TCP | 192.168.0.128:502 | TBC (meter address on SAU) | TBC | kWh | TBC | TBC | Cumulative delivered energy; check 32-bit word order
Voltage L1 N |  | Float |  | SAU-100 electric meter (LV PV panel) | Modbus TCP | 192.168.0.128:502 | TBC (meter address on SAU) | TBC | V | TBC | TBC
Voltage L2 N |  | Float |  | SAU-100 electric meter (LV PV panel) | Modbus TCP | 192.168.0.128:502 | TBC (meter address on SAU) | TBC | V | TBC | TBC
Voltage L3 N |  | Float |  | SAU-100 electric meter (LV PV panel) | Modbus TCP | 192.168.0.128:502 | TBC (meter address on SAU) | TBC | V | TBC | TBC
Panel Temperature |  | Word |  | SAU-100 environmental input (weather station) — TBC | Modbus TCP | 192.168.0.128:502 | TBC | TBC | °C | TBC | TBC | Confirm sensor exists and where it is wired
Pyranometer |  | Word |  | SAU-100 environmental input (weather station) — TBC | Modbus TCP | 192.168.0.128:502 | TBC | TBC | W/m² | TBC | TBC | Confirm sensor exists and where it is wired
Area_Connection_Error |  | Boolean |  | ComAp InteliNeo 5500 | Modbus TCP | 192.168.0.112:502 | TBC (InteliNeo Modbus address) | TBC |  | TBC | TBC | Suggest: InteliNeo 'PV Logger group 1/2 comm fail' warning bits (OR of both)
Thermal_Magnetic_Switch_On_(LV PANEL) |  | Boolean |  | ComAp InteliNeo 5500 | Modbus TCP | 192.168.0.112:502 | TBC (InteliNeo Modbus address) | TBC |  | TBC | TBC | PVCB closed feedback as read by InteliNeo binary input
Thermal_Magnetic_Switch_Off (LV PANEL) |  | Boolean |  | ComAp InteliNeo 5500 | Modbus TCP | 192.168.0.112:502 | TBC (InteliNeo Modbus address) | TBC |  | TBC | TBC | PVCB open feedback as read by InteliNeo binary input
Total_Energy |  | Word |  | SAU-100 electric meter (LV PV panel) | Modbus TCP | 192.168.0.128:502 | TBC (meter address on SAU) | TBC | kWh | TBC | TBC | Alternative: sum of INVn_TOTAL_PRODUCTION; data type 'Word' in template is too small for lifetime kWh — recommend 32-bit

## INFO
Item | Value / status
Site | Coca-Cola plant, Erbil — hybrid microgrid (grid + 5 gensets + PV)
Solar system vendor | Sineng Electric (inverters) — inverter model: TBC from nameplate
Number of inverters | 10 string inverters (template extended from 8 to 10)
PV gateway / logger | Sineng SAU-100, IP 192.168.0.128 (plant LAN), second interface 192.168.1.123; web UI http://192.168.0.128
Inverter ↔ SAU link | RS485 (Modbus RTU) from inverters to SAU, two groups; SAU exposes all inverters as Modbus TCP server on port 502
Other devices on SAU | Electric meter(s) and PID device(s) configured in SAU (seen in SAU device list) — details TBC
Existing monitoring | SAU local web UI (Device Monitor); ComAp InteliNeo 5500 master controller (IP 192.168.0.112) reads PV as 'PV Logger group 1/2' via Modbus TCP, unit address 245; plant SCADA PC; no cloud platform confirmed
ComAp data source | InteliNeo 5500 — Modbus TCP server; register list to be exported from InteliConfig (Modules → Modbus Registers). Gensets: 5 ComAp genset controllers; grid: 3 InteliMains 210
Protocols available | Modbus TCP (SAU, InteliNeo); Modbus RTU (inverters ↔ SAU, RS485); ComAp AirGate/WebSupervisor possible for InteliNeo (not enabled yet)
Data access status | Local LAN only today. The SAU Modbus server is already at its limit (send-queue congestion, comm-fail events in InteliNeo history, Oct 2026). ANY NEW POLLING OF THE SAU OR INTELINEO MUST BE COORDINATED — see NOTES
Documentation available | InteliNeo history exports, SAU diagnostics screenshots, integrator site-visit report (Stromatik, 28.09.2026). Still needed: Sineng inverter Modbus map, SAU point table, InteliConfig register export, single-line diagram
Technical contacts | Eng. Yousif (site); Sabir (data / monitoring integration); Stromatik Automation, Eng. Salwan (ComAp integrator); Sineng support (via site)
Revision | Rev.1.2 — structure and known values completed; register addresses marked TBC pending SAU point table and InteliConfig export

## NOTES
How to read this file
Yellow cells = value still to be confirmed (TBC). Green cells = confirmed from the site.
PLC_Address / Register = Modbus register on the source device. Convention: Modbus TCP, holding registers (FC03) unless stated; address as listed in the vendor point table (state 0-based or 1-based in Notes when known).
Where the missing addresses come from
1. Inverter signals: the Sineng SAU-100 web UI exports the Modbus point table for the connected inverters (Setting → communication / point table). Alternatively the Sineng inverter Modbus protocol document for the installed model. Unit ID per inverter = the inverter's address on the SAU.
2. Plant-level electrical signals (currents, voltages, P, Q, energy): from the electric meter connected to the SAU, or from the InteliNeo 5500 PV/bus measurements — whichever the site confirms as the official metering point.
3. Panel temperature / pyranometer: environmental sensors — confirm whether they are wired to the SAU (weather station input) or to another device.
4. Breaker states (LV panel thermal-magnetic switch): PVCB status as seen by the InteliNeo (binary input) — register from the InteliConfig Modbus register export.
5. ComAp values (PV prod, PV req, bus values, comm status): InteliConfig → Modules → Modbus Registers export of the InteliNeo configuration.
IMPORTANT for the monitoring integration
The SAU Modbus TCP server is single-threaded and is already overloaded by the InteliNeo polling (two sessions, 0 ms pause). Comm-fail events in the InteliNeo cause PV anti-islanding trips and bus under-voltage. Adding another Modbus client directly on the SAU or the InteliNeo will make this worse.
Recommended architecture: ONE local data collector on site reads the SAU and the InteliNeo gently (or reads the SCADA historian) and serves all consumers (DT Turkey monitoring, local dashboards) from its own database/OPC-UA/REST. No second poller on the field devices.
The 290 inverter tags (10 inverters × 29 signals) should be read in block reads per inverter, at ≥ 10 s interval, not tag-by-tag.