## Connection
Erbil solar plant - Modbus TCP register map for the CCI monitoring platform
Server | Plant data collector on the plant PC (read-only Modbus TCP server)
IP address | to be provided once the connection method (VPN) is agreed
Port | 502
Unit ID | 1
Function codes | 03 Read Holding Registers (04 returns the same registers). Writes are refused.
Addressing | 0-based protocol addresses (address 100 = holding register 40101 in 1-based notation)
Float tags | float32, 2 registers, high word first (ABCD), engineering units, scale 1
Boolean tags | uint16, 1 register, 0 / 1
Quality registers | one uint16 per tag at 1000 + index: 1 good, 2 stale, 0 bad / not available
Data refresh | values are read from the site devices once per hour (30 min at the fastest); please poll every 30-60 minutes
Register map version | 1
Header registers
0-1 | uint32 (high word first) | Unix time (UTC seconds) of the last site read
2 | uint16 | Minutes since the last site read (65535 = never)
3 | uint16 | Number of tags with quality good
4 | uint16 | Total number of tags (305)
5 | uint16 | Register map version
6 | uint16 | Heartbeat, +1 at every site read
Status column (Tags sheet) | Ready = the source signal is already wired; Pending commissioning = the address is fixed, the value stays at quality 0 until commissioning of that signal is complete

## Tags
# | Tag name | Address | Registers | Data type | Unit | Quality address | Source | Status
0 | INVERTER_1.INV1_AC_POWER | 100 | 2 | Float32 (ABCD) | kW | 1000 | inv-01.ac_power_kw | Pending commissioning
1 | INVERTER_1.INV1_CURRENT_I1 | 102 | 2 | Float32 (ABCD) | A | 1001 | inv-01.current_l1_a | Pending commissioning
2 | INVERTER_1.INV1_CURRENT_I2 | 104 | 2 | Float32 (ABCD) | A | 1002 | inv-01.current_l2_a | Pending commissioning
3 | INVERTER_1.INV1_CURRENT_I3 | 106 | 2 | Float32 (ABCD) | A | 1003 | inv-01.current_l3_a | Pending commissioning
4 | INVERTER_1.INV1_DC_POWER | 108 | 2 | Float32 (ABCD) | kW | 1004 | inv-01.dc_power_kw | Pending commissioning
5 | INVERTER_1.INV1_FREKANS | 110 | 2 | Float32 (ABCD) | Hz | 1005 | inv-01.frequency_hz | Pending commissioning
6 | INVERTER_1.INV1_VOLTAGE_V1 | 112 | 2 | Float32 (ABCD) | V | 1006 | inv-01.voltage_l1_v | Pending commissioning
7 | INVERTER_1.INV1_VOLTAGE_V2 | 114 | 2 | Float32 (ABCD) | V | 1007 | inv-01.voltage_l2_v | Pending commissioning
8 | INVERTER_1.INV1_VOLTAGE_V3 | 116 | 2 | Float32 (ABCD) | V | 1008 | inv-01.voltage_l3_v | Pending commissioning
9 | INVERTER_1.INV1_DAILY_PRODUCTION | 118 | 2 | Float32 (ABCD) | kWh | 1009 | inv-01.energy_today_kwh | Pending commissioning
10 | INVERTER_1.INV1_Connection_Error | 120 | 1 | Boolean (uint16 0/1) |  | 1010 | inv-01.comm_error | Pending commissioning
11 | INVERTER_1.INV1_String_CURRENT_I1 | 121 | 2 | Float32 (ABCD) | A | 1011 | inv-01.string_current_1_a | Pending commissioning
12 | INVERTER_1.INV1_String_CURRENT_I2 | 123 | 2 | Float32 (ABCD) | A | 1012 | inv-01.string_current_2_a | Pending commissioning
13 | INVERTER_1.INV1_String_CURRENT_I3 | 125 | 2 | Float32 (ABCD) | A | 1013 | inv-01.string_current_3_a | Pending commissioning
14 | INVERTER_1.INV1_String_CURRENT_I4 | 127 | 2 | Float32 (ABCD) | A | 1014 | inv-01.string_current_4_a | Pending commissioning
15 | INVERTER_1.INV1_String_CURRENT_I5 | 129 | 2 | Float32 (ABCD) | A | 1015 | inv-01.string_current_5_a | Pending commissioning
16 | INVERTER_1.INV1_String_CURRENT_I6 | 131 | 2 | Float32 (ABCD) | A | 1016 | inv-01.string_current_6_a | Pending commissioning
17 | INVERTER_1.INV1_String_CURRENT_I7 | 133 | 2 | Float32 (ABCD) | A | 1017 | inv-01.string_current_7_a | Pending commissioning
18 | INVERTER_1.INV1_String_CURRENT_I8 | 135 | 2 | Float32 (ABCD) | A | 1018 | inv-01.string_current_8_a | Pending commissioning
19 | INVERTER_1.INV1_String_CURRENT_I9 | 137 | 2 | Float32 (ABCD) | A | 1019 | inv-01.string_current_9_a | Pending commissioning
20 | INVERTER_1.INV1_String_CURRENT_I10 | 139 | 2 | Float32 (ABCD) | A | 1020 | inv-01.string_current_10_a | Pending commissioning
21 | INVERTER_1.INV1_String_CURRENT_I11 | 141 | 2 | Float32 (ABCD) | A | 1021 | inv-01.string_current_11_a | Pending commissioning
22 | INVERTER_1.INV1_String_CURRENT_I12 | 143 | 2 | Float32 (ABCD) | A | 1022 | inv-01.string_current_12_a | Pending commissioning
23 | INVERTER_1.INV1_String_CURRENT_I13 | 145 | 2 | Float32 (ABCD) | A | 1023 | inv-01.string_current_13_a | Pending commissioning
24 | INVERTER_1.INV1_String_CURRENT_I14 | 147 | 2 | Float32 (ABCD) | A | 1024 | inv-01.string_current_14_a | Pending commissioning
25 | INVERTER_1.INV1_String_CURRENT_I15 | 149 | 2 | Float32 (ABCD) | A | 1025 | inv-01.string_current_15_a | Pending commissioning
26 | INVERTER_1.INV1_String_CURRENT_I16 | 151 | 2 | Float32 (ABCD) | A | 1026 | inv-01.string_current_16_a | Pending commissioning
27 | INVERTER_1.INV1_String_CURRENT_I17 | 153 | 2 | Float32 (ABCD) | A | 1027 | inv-01.string_current_17_a | Pending commissioning
28 | INVERTER_1.INV1_TOTAL_PRODUCTION | 155 | 2 | Float32 (ABCD) | kWh | 1028 | inv-01.energy_total_kwh | Pending commissioning
29 | INVERTER_2.INV2_AC_POWER | 157 | 2 | Float32 (ABCD) | kW | 1029 | inv-02.ac_power_kw | Pending commissioning
30 | INVERTER_2.INV2_CURRENT_I1 | 159 | 2 | Float32 (ABCD) | A | 1030 | inv-02.current_l1_a | Pending commissioning
31 | INVERTER_2.INV2_CURRENT_I2 | 161 | 2 | Float32 (ABCD) | A | 1031 | inv-02.current_l2_a | Pending commissioning
32 | INVERTER_2.INV2_CURRENT_I3 | 163 | 2 | Float32 (ABCD) | A | 1032 | inv-02.current_l3_a | Pending commissioning
33 | INVERTER_2.INV2_DC_POWER | 165 | 2 | Float32 (ABCD) | kW | 1033 | inv-02.dc_power_kw | Pending commissioning
34 | INVERTER_2.INV2_FREKANS | 167 | 2 | Float32 (ABCD) | Hz | 1034 | inv-02.frequency_hz | Pending commissioning
35 | INVERTER_2.INV2_VOLTAGE_V1 | 169 | 2 | Float32 (ABCD) | V | 1035 | inv-02.voltage_l1_v | Pending commissioning
36 | INVERTER_2.INV2_VOLTAGE_V2 | 171 | 2 | Float32 (ABCD) | V | 1036 | inv-02.voltage_l2_v | Pending commissioning
37 | INVERTER_2.INV2_VOLTAGE_V3 | 173 | 2 | Float32 (ABCD) | V | 1037 | inv-02.voltage_l3_v | Pending commissioning
38 | INVERTER_2.INV2_DAILY_PRODUCTION | 175 | 2 | Float32 (ABCD) | kWh | 1038 | inv-02.energy_today_kwh | Pending commissioning
39 | INVERTER_2.INV2_Connection_Error | 177 | 1 | Boolean (uint16 0/1) |  | 1039 | inv-02.comm_error | Pending commissioning
40 | INVERTER_2.INV2_String_CURRENT_I1 | 178 | 2 | Float32 (ABCD) | A | 1040 | inv-02.string_current_1_a | Pending commissioning
41 | INVERTER_2.INV2_String_CURRENT_I2 | 180 | 2 | Float32 (ABCD) | A | 1041 | inv-02.string_current_2_a | Pending commissioning
42 | INVERTER_2.INV2_String_CURRENT_I3 | 182 | 2 | Float32 (ABCD) | A | 1042 | inv-02.string_current_3_a | Pending commissioning
43 | INVERTER_2.INV2_String_CURRENT_I4 | 184 | 2 | Float32 (ABCD) | A | 1043 | inv-02.string_current_4_a | Pending commissioning
44 | INVERTER_2.INV2_String_CURRENT_I5 | 186 | 2 | Float32 (ABCD) | A | 1044 | inv-02.string_current_5_a | Pending commissioning
45 | INVERTER_2.INV2_String_CURRENT_I6 | 188 | 2 | Float32 (ABCD) | A | 1045 | inv-02.string_current_6_a | Pending commissioning
46 | INVERTER_2.INV2_String_CURRENT_I7 | 190 | 2 | Float32 (ABCD) | A | 1046 | inv-02.string_current_7_a | Pending commissioning
47 | INVERTER_2.INV2_String_CURRENT_I8 | 192 | 2 | Float32 (ABCD) | A | 1047 | inv-02.string_current_8_a | Pending commissioning
48 | INVERTER_2.INV2_String_CURRENT_I9 | 194 | 2 | Float32 (ABCD) | A | 1048 | inv-02.string_current_9_a | Pending commissioning
49 | INVERTER_2.INV2_String_CURRENT_I10 | 196 | 2 | Float32 (ABCD) | A | 1049 | inv-02.string_current_10_a | Pending commissioning
50 | INVERTER_2.INV2_String_CURRENT_I11 | 198 | 2 | Float32 (ABCD) | A | 1050 | inv-02.string_current_11_a | Pending commissioning
51 | INVERTER_2.INV2_String_CURRENT_I12 | 200 | 2 | Float32 (ABCD) | A | 1051 | inv-02.string_current_12_a | Pending commissioning
52 | INVERTER_2.INV2_String_CURRENT_I13 | 202 | 2 | Float32 (ABCD) | A | 1052 | inv-02.string_current_13_a | Pending commissioning
53 | INVERTER_2.INV2_String_CURRENT_I14 | 204 | 2 | Float32 (ABCD) | A | 1053 | inv-02.string_current_14_a | Pending commissioning
54 | INVERTER_2.INV2_String_CURRENT_I15 | 206 | 2 | Float32 (ABCD) | A | 1054 | inv-02.string_current_15_a | Pending commissioning
55 | INVERTER_2.INV2_String_CURRENT_I16 | 208 | 2 | Float32 (ABCD) | A | 1055 | inv-02.string_current_16_a | Pending commissioning
56 | INVERTER_2.INV2_String_CURRENT_I17 | 210 | 2 | Float32 (ABCD) | A | 1056 | inv-02.string_current_17_a | Pending commissioning
57 | INVERTER_2.INV2_TOTAL_PRODUCTION | 212 | 2 | Float32 (ABCD) | kWh | 1057 | inv-02.energy_total_kwh | Pending commissioning
58 | INVERTER_3.INV3_AC_POWER | 214 | 2 | Float32 (ABCD) | kW | 1058 | inv-03.ac_power_kw | Pending commissioning
59 | INVERTER_3.INV3_CURRENT_I1 | 216 | 2 | Float32 (ABCD) | A | 1059 | inv-03.current_l1_a | Pending commissioning
60 | INVERTER_3.INV3_CURRENT_I2 | 218 | 2 | Float32 (ABCD) | A | 1060 | inv-03.current_l2_a | Pending commissioning
61 | INVERTER_3.INV3_CURRENT_I3 | 220 | 2 | Float32 (ABCD) | A | 1061 | inv-03.current_l3_a | Pending commissioning
62 | INVERTER_3.INV3_DC_POWER | 222 | 2 | Float32 (ABCD) | kW | 1062 | inv-03.dc_power_kw | Pending commissioning
63 | INVERTER_3.INV3_FREKANS | 224 | 2 | Float32 (ABCD) | Hz | 1063 | inv-03.frequency_hz | Pending commissioning
64 | INVERTER_3.INV3_VOLTAGE_V1 | 226 | 2 | Float32 (ABCD) | V | 1064 | inv-03.voltage_l1_v | Pending commissioning
65 | INVERTER_3.INV3_VOLTAGE_V2 | 228 | 2 | Float32 (ABCD) | V | 1065 | inv-03.voltage_l2_v | Pending commissioning
66 | INVERTER_3.INV3_VOLTAGE_V3 | 230 | 2 | Float32 (ABCD) | V | 1066 | inv-03.voltage_l3_v | Pending commissioning
67 | INVERTER_3.INV3_DAILY_PRODUCTION | 232 | 2 | Float32 (ABCD) | kWh | 1067 | inv-03.energy_today_kwh | Pending commissioning
68 | INVERTER_3.INV3_Connection_Error | 234 | 1 | Boolean (uint16 0/1) |  | 1068 | inv-03.comm_error | Pending commissioning
69 | INVERTER_3.INV3_String_CURRENT_I1 | 235 | 2 | Float32 (ABCD) | A | 1069 | inv-03.string_current_1_a | Pending commissioning
70 | INVERTER_3.INV3_String_CURRENT_I2 | 237 | 2 | Float32 (ABCD) | A | 1070 | inv-03.string_current_2_a | Pending commissioning
71 | INVERTER_3.INV3_String_CURRENT_I3 | 239 | 2 | Float32 (ABCD) | A | 1071 | inv-03.string_current_3_a | Pending commissioning
72 | INVERTER_3.INV3_String_CURRENT_I4 | 241 | 2 | Float32 (ABCD) | A | 1072 | inv-03.string_current_4_a | Pending commissioning
73 | INVERTER_3.INV3_String_CURRENT_I5 | 243 | 2 | Float32 (ABCD) | A | 1073 | inv-03.string_current_5_a | Pending commissioning
74 | INVERTER_3.INV3_String_CURRENT_I6 | 245 | 2 | Float32 (ABCD) | A | 1074 | inv-03.string_current_6_a | Pending commissioning
75 | INVERTER_3.INV3_String_CURRENT_I7 | 247 | 2 | Float32 (ABCD) | A | 1075 | inv-03.string_current_7_a | Pending commissioning
76 | INVERTER_3.INV3_String_CURRENT_I8 | 249 | 2 | Float32 (ABCD) | A | 1076 | inv-03.string_current_8_a | Pending commissioning
77 | INVERTER_3.INV3_String_CURRENT_I9 | 251 | 2 | Float32 (ABCD) | A | 1077 | inv-03.string_current_9_a | Pending commissioning
78 | INVERTER_3.INV3_String_CURRENT_I10 | 253 | 2 | Float32 (ABCD) | A | 1078 | inv-03.string_current_10_a | Pending commissioning
79 | INVERTER_3.INV3_String_CURRENT_I11 | 255 | 2 | Float32 (ABCD) | A | 1079 | inv-03.string_current_11_a | Pending commissioning
80 | INVERTER_3.INV3_String_CURRENT_I12 | 257 | 2 | Float32 (ABCD) | A | 1080 | inv-03.string_current_12_a | Pending commissioning
81 | INVERTER_3.INV3_String_CURRENT_I13 | 259 | 2 | Float32 (ABCD) | A | 1081 | inv-03.string_current_13_a | Pending commissioning
82 | INVERTER_3.INV3_String_CURRENT_I14 | 261 | 2 | Float32 (ABCD) | A | 1082 | inv-03.string_current_14_a | Pending commissioning
83 | INVERTER_3.INV3_String_CURRENT_I15 | 263 | 2 | Float32 (ABCD) | A | 1083 | inv-03.string_current_15_a | Pending commissioning
84 | INVERTER_3.INV3_String_CURRENT_I16 | 265 | 2 | Float32 (ABCD) | A | 1084 | inv-03.string_current_16_a | Pending commissioning
85 | INVERTER_3.INV3_String_CURRENT_I17 | 267 | 2 | Float32 (ABCD) | A | 1085 | inv-03.string_current_17_a | Pending commissioning
86 | INVERTER_3.INV3_TOTAL_PRODUCTION | 269 | 2 | Float32 (ABCD) | kWh | 1086 | inv-03.energy_total_kwh | Pending commissioning
87 | INVERTER_4.INV4_AC_POWER | 271 | 2 | Float32 (ABCD) | kW | 1087 | inv-04.ac_power_kw | Pending commissioning
88 | INVERTER_4.INV4_CURRENT_I1 | 273 | 2 | Float32 (ABCD) | A | 1088 | inv-04.current_l1_a | Pending commissioning
89 | INVERTER_4.INV4_CURRENT_I2 | 275 | 2 | Float32 (ABCD) | A | 1089 | inv-04.current_l2_a | Pending commissioning
90 | INVERTER_4.INV4_CURRENT_I3 | 277 | 2 | Float32 (ABCD) | A | 1090 | inv-04.current_l3_a | Pending commissioning
91 | INVERTER_4.INV4_DC_POWER | 279 | 2 | Float32 (ABCD) | kW | 1091 | inv-04.dc_power_kw | Pending commissioning
92 | INVERTER_4.INV4_FREKANS | 281 | 2 | Float32 (ABCD) | Hz | 1092 | inv-04.frequency_hz | Pending commissioning
93 | INVERTER_4.INV4_VOLTAGE_V1 | 283 | 2 | Float32 (ABCD) | V | 1093 | inv-04.voltage_l1_v | Pending commissioning
94 | INVERTER_4.INV4_VOLTAGE_V2 | 285 | 2 | Float32 (ABCD) | V | 1094 | inv-04.voltage_l2_v | Pending commissioning
95 | INVERTER_4.INV4_VOLTAGE_V3 | 287 | 2 | Float32 (ABCD) | V | 1095 | inv-04.voltage_l3_v | Pending commissioning
96 | INVERTER_4.INV4_DAILY_PRODUCTION | 289 | 2 | Float32 (ABCD) | kWh | 1096 | inv-04.energy_today_kwh | Pending commissioning
97 | INVERTER_4.INV4_Connection_Error | 291 | 1 | Boolean (uint16 0/1) |  | 1097 | inv-04.comm_error | Pending commissioning
98 | INVERTER_4.INV4_String_CURRENT_I1 | 292 | 2 | Float32 (ABCD) | A | 1098 | inv-04.string_current_1_a | Pending commissioning
99 | INVERTER_4.INV4_String_CURRENT_I2 | 294 | 2 | Float32 (ABCD) | A | 1099 | inv-04.string_current_2_a | Pending commissioning
100 | INVERTER_4.INV4_String_CURRENT_I3 | 296 | 2 | Float32 (ABCD) | A | 1100 | inv-04.string_current_3_a | Pending commissioning
101 | INVERTER_4.INV4_String_CURRENT_I4 | 298 | 2 | Float32 (ABCD) | A | 1101 | inv-04.string_current_4_a | Pending commissioning
102 | INVERTER_4.INV4_String_CURRENT_I5 | 300 | 2 | Float32 (ABCD) | A | 1102 | inv-04.string_current_5_a | Pending commissioning
103 | INVERTER_4.INV4_String_CURRENT_I6 | 302 | 2 | Float32 (ABCD) | A | 1103 | inv-04.string_current_6_a | Pending commissioning
104 | INVERTER_4.INV4_String_CURRENT_I7 | 304 | 2 | Float32 (ABCD) | A | 1104 | inv-04.string_current_7_a | Pending commissioning
105 | INVERTER_4.INV4_String_CURRENT_I8 | 306 | 2 | Float32 (ABCD) | A | 1105 | inv-04.string_current_8_a | Pending commissioning
106 | INVERTER_4.INV4_String_CURRENT_I9 | 308 | 2 | Float32 (ABCD) | A | 1106 | inv-04.string_current_9_a | Pending commissioning
107 | INVERTER_4.INV4_String_CURRENT_I10 | 310 | 2 | Float32 (ABCD) | A | 1107 | inv-04.string_current_10_a | Pending commissioning
108 | INVERTER_4.INV4_String_CURRENT_I11 | 312 | 2 | Float32 (ABCD) | A | 1108 | inv-04.string_current_11_a | Pending commissioning
109 | INVERTER_4.INV4_String_CURRENT_I12 | 314 | 2 | Float32 (ABCD) | A | 1109 | inv-04.string_current_12_a | Pending commissioning
110 | INVERTER_4.INV4_String_CURRENT_I13 | 316 | 2 | Float32 (ABCD) | A | 1110 | inv-04.string_current_13_a | Pending commissioning
111 | INVERTER_4.INV4_String_CURRENT_I14 | 318 | 2 | Float32 (ABCD) | A | 1111 | inv-04.string_current_14_a | Pending commissioning
112 | INVERTER_4.INV4_String_CURRENT_I15 | 320 | 2 | Float32 (ABCD) | A | 1112 | inv-04.string_current_15_a | Pending commissioning
113 | INVERTER_4.INV4_String_CURRENT_I16 | 322 | 2 | Float32 (ABCD) | A | 1113 | inv-04.string_current_16_a | Pending commissioning
114 | INVERTER_4.INV4_String_CURRENT_I17 | 324 | 2 | Float32 (ABCD) | A | 1114 | inv-04.string_current_17_a | Pending commissioning
115 | INVERTER_4.INV4_TOTAL_PRODUCTION | 326 | 2 | Float32 (ABCD) | kWh | 1115 | inv-04.energy_total_kwh | Pending commissioning
116 | INVERTER_5.INV5_AC_POWER | 328 | 2 | Float32 (ABCD) | kW | 1116 | inv-05.ac_power_kw | Pending commissioning
117 | INVERTER_5.INV5_CURRENT_I1 | 330 | 2 | Float32 (ABCD) | A | 1117 | inv-05.current_l1_a | Pending commissioning
118 | INVERTER_5.INV5_CURRENT_I2 | 332 | 2 | Float32 (ABCD) | A | 1118 | inv-05.current_l2_a | Pending commissioning
119 | INVERTER_5.INV5_CURRENT_I3 | 334 | 2 | Float32 (ABCD) | A | 1119 | inv-05.current_l3_a | Pending commissioning
120 | INVERTER_5.INV5_DC_POWER | 336 | 2 | Float32 (ABCD) | kW | 1120 | inv-05.dc_power_kw | Pending commissioning
121 | INVERTER_5.INV5_FREKANS | 338 | 2 | Float32 (ABCD) | Hz | 1121 | inv-05.frequency_hz | Pending commissioning
122 | INVERTER_5.INV5_VOLTAGE_V1 | 340 | 2 | Float32 (ABCD) | V | 1122 | inv-05.voltage_l1_v | Pending commissioning
123 | INVERTER_5.INV5_VOLTAGE_V2 | 342 | 2 | Float32 (ABCD) | V | 1123 | inv-05.voltage_l2_v | Pending commissioning
124 | INVERTER_5.INV5_VOLTAGE_V3 | 344 | 2 | Float32 (ABCD) | V | 1124 | inv-05.voltage_l3_v | Pending commissioning
125 | INVERTER_5.INV5_DAILY_PRODUCTION | 346 | 2 | Float32 (ABCD) | kWh | 1125 | inv-05.energy_today_kwh | Pending commissioning
126 | INVERTER_5.INV5_Connection_Error | 348 | 1 | Boolean (uint16 0/1) |  | 1126 | inv-05.comm_error | Pending commissioning
127 | INVERTER_5.INV5_String_CURRENT_I1 | 349 | 2 | Float32 (ABCD) | A | 1127 | inv-05.string_current_1_a | Pending commissioning
128 | INVERTER_5.INV5_String_CURRENT_I2 | 351 | 2 | Float32 (ABCD) | A | 1128 | inv-05.string_current_2_a | Pending commissioning
129 | INVERTER_5.INV5_String_CURRENT_I3 | 353 | 2 | Float32 (ABCD) | A | 1129 | inv-05.string_current_3_a | Pending commissioning
130 | INVERTER_5.INV5_String_CURRENT_I4 | 355 | 2 | Float32 (ABCD) | A | 1130 | inv-05.string_current_4_a | Pending commissioning
131 | INVERTER_5.INV5_String_CURRENT_I5 | 357 | 2 | Float32 (ABCD) | A | 1131 | inv-05.string_current_5_a | Pending commissioning
132 | INVERTER_5.INV5_String_CURRENT_I6 | 359 | 2 | Float32 (ABCD) | A | 1132 | inv-05.string_current_6_a | Pending commissioning
133 | INVERTER_5.INV5_String_CURRENT_I7 | 361 | 2 | Float32 (ABCD) | A | 1133 | inv-05.string_current_7_a | Pending commissioning
134 | INVERTER_5.INV5_String_CURRENT_I8 | 363 | 2 | Float32 (ABCD) | A | 1134 | inv-05.string_current_8_a | Pending commissioning
135 | INVERTER_5.INV5_String_CURRENT_I9 | 365 | 2 | Float32 (ABCD) | A | 1135 | inv-05.string_current_9_a | Pending commissioning
136 | INVERTER_5.INV5_String_CURRENT_I10 | 367 | 2 | Float32 (ABCD) | A | 1136 | inv-05.string_current_10_a | Pending commissioning
137 | INVERTER_5.INV5_String_CURRENT_I11 | 369 | 2 | Float32 (ABCD) | A | 1137 | inv-05.string_current_11_a | Pending commissioning
138 | INVERTER_5.INV5_String_CURRENT_I12 | 371 | 2 | Float32 (ABCD) | A | 1138 | inv-05.string_current_12_a | Pending commissioning
139 | INVERTER_5.INV5_String_CURRENT_I13 | 373 | 2 | Float32 (ABCD) | A | 1139 | inv-05.string_current_13_a | Pending commissioning
140 | INVERTER_5.INV5_String_CURRENT_I14 | 375 | 2 | Float32 (ABCD) | A | 1140 | inv-05.string_current_14_a | Pending commissioning
141 | INVERTER_5.INV5_String_CURRENT_I15 | 377 | 2 | Float32 (ABCD) | A | 1141 | inv-05.string_current_15_a | Pending commissioning
142 | INVERTER_5.INV5_String_CURRENT_I16 | 379 | 2 | Float32 (ABCD) | A | 1142 | inv-05.string_current_16_a | Pending commissioning
143 | INVERTER_5.INV5_String_CURRENT_I17 | 381 | 2 | Float32 (ABCD) | A | 1143 | inv-05.string_current_17_a | Pending commissioning
144 | INVERTER_5.INV5_TOTAL_PRODUCTION | 383 | 2 | Float32 (ABCD) | kWh | 1144 | inv-05.energy_total_kwh | Pending commissioning
145 | INVERTER_6.INV6_AC_POWER | 385 | 2 | Float32 (ABCD) | kW | 1145 | inv-06.ac_power_kw | Pending commissioning
146 | INVERTER_6.INV6_CURRENT_I1 | 387 | 2 | Float32 (ABCD) | A | 1146 | inv-06.current_l1_a | Pending commissioning
147 | INVERTER_6.INV6_CURRENT_I2 | 389 | 2 | Float32 (ABCD) | A | 1147 | inv-06.current_l2_a | Pending commissioning
148 | INVERTER_6.INV6_CURRENT_I3 | 391 | 2 | Float32 (ABCD) | A | 1148 | inv-06.current_l3_a | Pending commissioning
149 | INVERTER_6.INV6_DC_POWER | 393 | 2 | Float32 (ABCD) | kW | 1149 | inv-06.dc_power_kw | Pending commissioning
150 | INVERTER_6.INV6_FREKANS | 395 | 2 | Float32 (ABCD) | Hz | 1150 | inv-06.frequency_hz | Pending commissioning
151 | INVERTER_6.INV6_VOLTAGE_V1 | 397 | 2 | Float32 (ABCD) | V | 1151 | inv-06.voltage_l1_v | Pending commissioning
152 | INVERTER_6.INV6_VOLTAGE_V2 | 399 | 2 | Float32 (ABCD) | V | 1152 | inv-06.voltage_l2_v | Pending commissioning
153 | INVERTER_6.INV6_VOLTAGE_V3 | 401 | 2 | Float32 (ABCD) | V | 1153 | inv-06.voltage_l3_v | Pending commissioning
154 | INVERTER_6.INV6_DAILY_PRODUCTION | 403 | 2 | Float32 (ABCD) | kWh | 1154 | inv-06.energy_today_kwh | Pending commissioning
155 | INVERTER_6.INV6_Connection_Error | 405 | 1 | Boolean (uint16 0/1) |  | 1155 | inv-06.comm_error | Pending commissioning
156 | INVERTER_6.INV6_String_CURRENT_I1 | 406 | 2 | Float32 (ABCD) | A | 1156 | inv-06.string_current_1_a | Pending commissioning
157 | INVERTER_6.INV6_String_CURRENT_I2 | 408 | 2 | Float32 (ABCD) | A | 1157 | inv-06.string_current_2_a | Pending commissioning
158 | INVERTER_6.INV6_String_CURRENT_I3 | 410 | 2 | Float32 (ABCD) | A | 1158 | inv-06.string_current_3_a | Pending commissioning
159 | INVERTER_6.INV6_String_CURRENT_I4 | 412 | 2 | Float32 (ABCD) | A | 1159 | inv-06.string_current_4_a | Pending commissioning
160 | INVERTER_6.INV6_String_CURRENT_I5 | 414 | 2 | Float32 (ABCD) | A | 1160 | inv-06.string_current_5_a | Pending commissioning
161 | INVERTER_6.INV6_String_CURRENT_I6 | 416 | 2 | Float32 (ABCD) | A | 1161 | inv-06.string_current_6_a | Pending commissioning
162 | INVERTER_6.INV6_String_CURRENT_I7 | 418 | 2 | Float32 (ABCD) | A | 1162 | inv-06.string_current_7_a | Pending commissioning
163 | INVERTER_6.INV6_String_CURRENT_I8 | 420 | 2 | Float32 (ABCD) | A | 1163 | inv-06.string_current_8_a | Pending commissioning
164 | INVERTER_6.INV6_String_CURRENT_I9 | 422 | 2 | Float32 (ABCD) | A | 1164 | inv-06.string_current_9_a | Pending commissioning
165 | INVERTER_6.INV6_String_CURRENT_I10 | 424 | 2 | Float32 (ABCD) | A | 1165 | inv-06.string_current_10_a | Pending commissioning
166 | INVERTER_6.INV6_String_CURRENT_I11 | 426 | 2 | Float32 (ABCD) | A | 1166 | inv-06.string_current_11_a | Pending commissioning
167 | INVERTER_6.INV6_String_CURRENT_I12 | 428 | 2 | Float32 (ABCD) | A | 1167 | inv-06.string_current_12_a | Pending commissioning
168 | INVERTER_6.INV6_String_CURRENT_I13 | 430 | 2 | Float32 (ABCD) | A | 1168 | inv-06.string_current_13_a | Pending commissioning
169 | INVERTER_6.INV6_String_CURRENT_I14 | 432 | 2 | Float32 (ABCD) | A | 1169 | inv-06.string_current_14_a | Pending commissioning
170 | INVERTER_6.INV6_String_CURRENT_I15 | 434 | 2 | Float32 (ABCD) | A | 1170 | inv-06.string_current_15_a | Pending commissioning
171 | INVERTER_6.INV6_String_CURRENT_I16 | 436 | 2 | Float32 (ABCD) | A | 1171 | inv-06.string_current_16_a | Pending commissioning
172 | INVERTER_6.INV6_String_CURRENT_I17 | 438 | 2 | Float32 (ABCD) | A | 1172 | inv-06.string_current_17_a | Pending commissioning
173 | INVERTER_6.INV6_TOTAL_PRODUCTION | 440 | 2 | Float32 (ABCD) | kWh | 1173 | inv-06.energy_total_kwh | Pending commissioning
174 | INVERTER_7.INV7_AC_POWER | 442 | 2 | Float32 (ABCD) | kW | 1174 | inv-07.ac_power_kw | Pending commissioning
175 | INVERTER_7.INV7_CURRENT_I1 | 444 | 2 | Float32 (ABCD) | A | 1175 | inv-07.current_l1_a | Pending commissioning
176 | INVERTER_7.INV7_CURRENT_I2 | 446 | 2 | Float32 (ABCD) | A | 1176 | inv-07.current_l2_a | Pending commissioning
177 | INVERTER_7.INV7_CURRENT_I3 | 448 | 2 | Float32 (ABCD) | A | 1177 | inv-07.current_l3_a | Pending commissioning
178 | INVERTER_7.INV7_DC_POWER | 450 | 2 | Float32 (ABCD) | kW | 1178 | inv-07.dc_power_kw | Pending commissioning
179 | INVERTER_7.INV7_FREKANS | 452 | 2 | Float32 (ABCD) | Hz | 1179 | inv-07.frequency_hz | Pending commissioning
180 | INVERTER_7.INV7_VOLTAGE_V1 | 454 | 2 | Float32 (ABCD) | V | 1180 | inv-07.voltage_l1_v | Pending commissioning
181 | INVERTER_7.INV7_VOLTAGE_V2 | 456 | 2 | Float32 (ABCD) | V | 1181 | inv-07.voltage_l2_v | Pending commissioning
182 | INVERTER_7.INV7_VOLTAGE_V3 | 458 | 2 | Float32 (ABCD) | V | 1182 | inv-07.voltage_l3_v | Pending commissioning
183 | INVERTER_7.INV7_DAILY_PRODUCTION | 460 | 2 | Float32 (ABCD) | kWh | 1183 | inv-07.energy_today_kwh | Pending commissioning
184 | INVERTER_7.INV7_Connection_Error | 462 | 1 | Boolean (uint16 0/1) |  | 1184 | inv-07.comm_error | Pending commissioning
185 | INVERTER_7.INV7_String_CURRENT_I1 | 463 | 2 | Float32 (ABCD) | A | 1185 | inv-07.string_current_1_a | Pending commissioning
186 | INVERTER_7.INV7_String_CURRENT_I2 | 465 | 2 | Float32 (ABCD) | A | 1186 | inv-07.string_current_2_a | Pending commissioning
187 | INVERTER_7.INV7_String_CURRENT_I3 | 467 | 2 | Float32 (ABCD) | A | 1187 | inv-07.string_current_3_a | Pending commissioning
188 | INVERTER_7.INV7_String_CURRENT_I4 | 469 | 2 | Float32 (ABCD) | A | 1188 | inv-07.string_current_4_a | Pending commissioning
189 | INVERTER_7.INV7_String_CURRENT_I5 | 471 | 2 | Float32 (ABCD) | A | 1189 | inv-07.string_current_5_a | Pending commissioning
190 | INVERTER_7.INV7_String_CURRENT_I6 | 473 | 2 | Float32 (ABCD) | A | 1190 | inv-07.string_current_6_a | Pending commissioning
191 | INVERTER_7.INV7_String_CURRENT_I7 | 475 | 2 | Float32 (ABCD) | A | 1191 | inv-07.string_current_7_a | Pending commissioning
192 | INVERTER_7.INV7_String_CURRENT_I8 | 477 | 2 | Float32 (ABCD) | A | 1192 | inv-07.string_current_8_a | Pending commissioning
193 | INVERTER_7.INV7_String_CURRENT_I9 | 479 | 2 | Float32 (ABCD) | A | 1193 | inv-07.string_current_9_a | Pending commissioning
194 | INVERTER_7.INV7_String_CURRENT_I10 | 481 | 2 | Float32 (ABCD) | A | 1194 | inv-07.string_current_10_a | Pending commissioning
195 | INVERTER_7.INV7_String_CURRENT_I11 | 483 | 2 | Float32 (ABCD) | A | 1195 | inv-07.string_current_11_a | Pending commissioning
196 | INVERTER_7.INV7_String_CURRENT_I12 | 485 | 2 | Float32 (ABCD) | A | 1196 | inv-07.string_current_12_a | Pending commissioning
197 | INVERTER_7.INV7_String_CURRENT_I13 | 487 | 2 | Float32 (ABCD) | A | 1197 | inv-07.string_current_13_a | Pending commissioning
198 | INVERTER_7.INV7_String_CURRENT_I14 | 489 | 2 | Float32 (ABCD) | A | 1198 | inv-07.string_current_14_a | Pending commissioning
199 | INVERTER_7.INV7_String_CURRENT_I15 | 491 | 2 | Float32 (ABCD) | A | 1199 | inv-07.string_current_15_a | Pending commissioning
200 | INVERTER_7.INV7_String_CURRENT_I16 | 493 | 2 | Float32 (ABCD) | A | 1200 | inv-07.string_current_16_a | Pending commissioning
201 | INVERTER_7.INV7_String_CURRENT_I17 | 495 | 2 | Float32 (ABCD) | A | 1201 | inv-07.string_current_17_a | Pending commissioning
202 | INVERTER_7.INV7_TOTAL_PRODUCTION | 497 | 2 | Float32 (ABCD) | kWh | 1202 | inv-07.energy_total_kwh | Pending commissioning
203 | INVERTER_8.INV8_AC_POWER | 499 | 2 | Float32 (ABCD) | kW | 1203 | inv-08.ac_power_kw | Pending commissioning
204 | INVERTER_8.INV8_CURRENT_I1 | 501 | 2 | Float32 (ABCD) | A | 1204 | inv-08.current_l1_a | Pending commissioning
205 | INVERTER_8.INV8_CURRENT_I2 | 503 | 2 | Float32 (ABCD) | A | 1205 | inv-08.current_l2_a | Pending commissioning
206 | INVERTER_8.INV8_CURRENT_I3 | 505 | 2 | Float32 (ABCD) | A | 1206 | inv-08.current_l3_a | Pending commissioning
207 | INVERTER_8.INV8_DC_POWER | 507 | 2 | Float32 (ABCD) | kW | 1207 | inv-08.dc_power_kw | Pending commissioning
208 | INVERTER_8.INV8_FREKANS | 509 | 2 | Float32 (ABCD) | Hz | 1208 | inv-08.frequency_hz | Pending commissioning
209 | INVERTER_8.INV8_VOLTAGE_V1 | 511 | 2 | Float32 (ABCD) | V | 1209 | inv-08.voltage_l1_v | Pending commissioning
210 | INVERTER_8.INV8_VOLTAGE_V2 | 513 | 2 | Float32 (ABCD) | V | 1210 | inv-08.voltage_l2_v | Pending commissioning
211 | INVERTER_8.INV8_VOLTAGE_V3 | 515 | 2 | Float32 (ABCD) | V | 1211 | inv-08.voltage_l3_v | Pending commissioning
212 | INVERTER_8.INV8_DAILY_PRODUCTION | 517 | 2 | Float32 (ABCD) | kWh | 1212 | inv-08.energy_today_kwh | Pending commissioning
213 | INVERTER_8.INV8_Connection_Error | 519 | 1 | Boolean (uint16 0/1) |  | 1213 | inv-08.comm_error | Pending commissioning
214 | INVERTER_8.INV8_String_CURRENT_I1 | 520 | 2 | Float32 (ABCD) | A | 1214 | inv-08.string_current_1_a | Pending commissioning
215 | INVERTER_8.INV8_String_CURRENT_I2 | 522 | 2 | Float32 (ABCD) | A | 1215 | inv-08.string_current_2_a | Pending commissioning
216 | INVERTER_8.INV8_String_CURRENT_I3 | 524 | 2 | Float32 (ABCD) | A | 1216 | inv-08.string_current_3_a | Pending commissioning
217 | INVERTER_8.INV8_String_CURRENT_I4 | 526 | 2 | Float32 (ABCD) | A | 1217 | inv-08.string_current_4_a | Pending commissioning
218 | INVERTER_8.INV8_String_CURRENT_I5 | 528 | 2 | Float32 (ABCD) | A | 1218 | inv-08.string_current_5_a | Pending commissioning
219 | INVERTER_8.INV8_String_CURRENT_I6 | 530 | 2 | Float32 (ABCD) | A | 1219 | inv-08.string_current_6_a | Pending commissioning
220 | INVERTER_8.INV8_String_CURRENT_I7 | 532 | 2 | Float32 (ABCD) | A | 1220 | inv-08.string_current_7_a | Pending commissioning
221 | INVERTER_8.INV8_String_CURRENT_I8 | 534 | 2 | Float32 (ABCD) | A | 1221 | inv-08.string_current_8_a | Pending commissioning
222 | INVERTER_8.INV8_String_CURRENT_I9 | 536 | 2 | Float32 (ABCD) | A | 1222 | inv-08.string_current_9_a | Pending commissioning
223 | INVERTER_8.INV8_String_CURRENT_I10 | 538 | 2 | Float32 (ABCD) | A | 1223 | inv-08.string_current_10_a | Pending commissioning
224 | INVERTER_8.INV8_String_CURRENT_I11 | 540 | 2 | Float32 (ABCD) | A | 1224 | inv-08.string_current_11_a | Pending commissioning
225 | INVERTER_8.INV8_String_CURRENT_I12 | 542 | 2 | Float32 (ABCD) | A | 1225 | inv-08.string_current_12_a | Pending commissioning
226 | INVERTER_8.INV8_String_CURRENT_I13 | 544 | 2 | Float32 (ABCD) | A | 1226 | inv-08.string_current_13_a | Pending commissioning
227 | INVERTER_8.INV8_String_CURRENT_I14 | 546 | 2 | Float32 (ABCD) | A | 1227 | inv-08.string_current_14_a | Pending commissioning
228 | INVERTER_8.INV8_String_CURRENT_I15 | 548 | 2 | Float32 (ABCD) | A | 1228 | inv-08.string_current_15_a | Pending commissioning
229 | INVERTER_8.INV8_String_CURRENT_I16 | 550 | 2 | Float32 (ABCD) | A | 1229 | inv-08.string_current_16_a | Pending commissioning
230 | INVERTER_8.INV8_String_CURRENT_I17 | 552 | 2 | Float32 (ABCD) | A | 1230 | inv-08.string_current_17_a | Pending commissioning
231 | INVERTER_8.INV8_TOTAL_PRODUCTION | 554 | 2 | Float32 (ABCD) | kWh | 1231 | inv-08.energy_total_kwh | Pending commissioning
232 | INVERTER_9.INV9_AC_POWER | 556 | 2 | Float32 (ABCD) | kW | 1232 | inv-09.ac_power_kw | Pending commissioning
233 | INVERTER_9.INV9_CURRENT_I1 | 558 | 2 | Float32 (ABCD) | A | 1233 | inv-09.current_l1_a | Pending commissioning
234 | INVERTER_9.INV9_CURRENT_I2 | 560 | 2 | Float32 (ABCD) | A | 1234 | inv-09.current_l2_a | Pending commissioning
235 | INVERTER_9.INV9_CURRENT_I3 | 562 | 2 | Float32 (ABCD) | A | 1235 | inv-09.current_l3_a | Pending commissioning
236 | INVERTER_9.INV9_DC_POWER | 564 | 2 | Float32 (ABCD) | kW | 1236 | inv-09.dc_power_kw | Pending commissioning
237 | INVERTER_9.INV9_FREKANS | 566 | 2 | Float32 (ABCD) | Hz | 1237 | inv-09.frequency_hz | Pending commissioning
238 | INVERTER_9.INV9_VOLTAGE_V1 | 568 | 2 | Float32 (ABCD) | V | 1238 | inv-09.voltage_l1_v | Pending commissioning
239 | INVERTER_9.INV9_VOLTAGE_V2 | 570 | 2 | Float32 (ABCD) | V | 1239 | inv-09.voltage_l2_v | Pending commissioning
240 | INVERTER_9.INV9_VOLTAGE_V3 | 572 | 2 | Float32 (ABCD) | V | 1240 | inv-09.voltage_l3_v | Pending commissioning
241 | INVERTER_9.INV9_DAILY_PRODUCTION | 574 | 2 | Float32 (ABCD) | kWh | 1241 | inv-09.energy_today_kwh | Pending commissioning
242 | INVERTER_9.INV9_Connection_Error | 576 | 1 | Boolean (uint16 0/1) |  | 1242 | inv-09.comm_error | Pending commissioning
243 | INVERTER_9.INV9_String_CURRENT_I1 | 577 | 2 | Float32 (ABCD) | A | 1243 | inv-09.string_current_1_a | Pending commissioning
244 | INVERTER_9.INV9_String_CURRENT_I2 | 579 | 2 | Float32 (ABCD) | A | 1244 | inv-09.string_current_2_a | Pending commissioning
245 | INVERTER_9.INV9_String_CURRENT_I3 | 581 | 2 | Float32 (ABCD) | A | 1245 | inv-09.string_current_3_a | Pending commissioning
246 | INVERTER_9.INV9_String_CURRENT_I4 | 583 | 2 | Float32 (ABCD) | A | 1246 | inv-09.string_current_4_a | Pending commissioning
247 | INVERTER_9.INV9_String_CURRENT_I5 | 585 | 2 | Float32 (ABCD) | A | 1247 | inv-09.string_current_5_a | Pending commissioning
248 | INVERTER_9.INV9_String_CURRENT_I6 | 587 | 2 | Float32 (ABCD) | A | 1248 | inv-09.string_current_6_a | Pending commissioning
249 | INVERTER_9.INV9_String_CURRENT_I7 | 589 | 2 | Float32 (ABCD) | A | 1249 | inv-09.string_current_7_a | Pending commissioning
250 | INVERTER_9.INV9_String_CURRENT_I8 | 591 | 2 | Float32 (ABCD) | A | 1250 | inv-09.string_current_8_a | Pending commissioning
251 | INVERTER_9.INV9_String_CURRENT_I9 | 593 | 2 | Float32 (ABCD) | A | 1251 | inv-09.string_current_9_a | Pending commissioning
252 | INVERTER_9.INV9_String_CURRENT_I10 | 595 | 2 | Float32 (ABCD) | A | 1252 | inv-09.string_current_10_a | Pending commissioning
253 | INVERTER_9.INV9_String_CURRENT_I11 | 597 | 2 | Float32 (ABCD) | A | 1253 | inv-09.string_current_11_a | Pending commissioning
254 | INVERTER_9.INV9_String_CURRENT_I12 | 599 | 2 | Float32 (ABCD) | A | 1254 | inv-09.string_current_12_a | Pending commissioning
255 | INVERTER_9.INV9_String_CURRENT_I13 | 601 | 2 | Float32 (ABCD) | A | 1255 | inv-09.string_current_13_a | Pending commissioning
256 | INVERTER_9.INV9_String_CURRENT_I14 | 603 | 2 | Float32 (ABCD) | A | 1256 | inv-09.string_current_14_a | Pending commissioning
257 | INVERTER_9.INV9_String_CURRENT_I15 | 605 | 2 | Float32 (ABCD) | A | 1257 | inv-09.string_current_15_a | Pending commissioning
258 | INVERTER_9.INV9_String_CURRENT_I16 | 607 | 2 | Float32 (ABCD) | A | 1258 | inv-09.string_current_16_a | Pending commissioning
259 | INVERTER_9.INV9_String_CURRENT_I17 | 609 | 2 | Float32 (ABCD) | A | 1259 | inv-09.string_current_17_a | Pending commissioning
260 | INVERTER_9.INV9_TOTAL_PRODUCTION | 611 | 2 | Float32 (ABCD) | kWh | 1260 | inv-09.energy_total_kwh | Pending commissioning
261 | INVERTER_10.INV10_AC_POWER | 613 | 2 | Float32 (ABCD) | kW | 1261 | inv-10.ac_power_kw | Pending commissioning
262 | INVERTER_10.INV10_CURRENT_I1 | 615 | 2 | Float32 (ABCD) | A | 1262 | inv-10.current_l1_a | Pending commissioning
263 | INVERTER_10.INV10_CURRENT_I2 | 617 | 2 | Float32 (ABCD) | A | 1263 | inv-10.current_l2_a | Pending commissioning
264 | INVERTER_10.INV10_CURRENT_I3 | 619 | 2 | Float32 (ABCD) | A | 1264 | inv-10.current_l3_a | Pending commissioning
265 | INVERTER_10.INV10_DC_POWER | 621 | 2 | Float32 (ABCD) | kW | 1265 | inv-10.dc_power_kw | Pending commissioning
266 | INVERTER_10.INV10_FREKANS | 623 | 2 | Float32 (ABCD) | Hz | 1266 | inv-10.frequency_hz | Pending commissioning
267 | INVERTER_10.INV10_VOLTAGE_V1 | 625 | 2 | Float32 (ABCD) | V | 1267 | inv-10.voltage_l1_v | Pending commissioning
268 | INVERTER_10.INV10_VOLTAGE_V2 | 627 | 2 | Float32 (ABCD) | V | 1268 | inv-10.voltage_l2_v | Pending commissioning
269 | INVERTER_10.INV10_VOLTAGE_V3 | 629 | 2 | Float32 (ABCD) | V | 1269 | inv-10.voltage_l3_v | Pending commissioning
270 | INVERTER_10.INV10_DAILY_PRODUCTION | 631 | 2 | Float32 (ABCD) | kWh | 1270 | inv-10.energy_today_kwh | Pending commissioning
271 | INVERTER_10.INV10_Connection_Error | 633 | 1 | Boolean (uint16 0/1) |  | 1271 | inv-10.comm_error | Pending commissioning
272 | INVERTER_10.INV10_String_CURRENT_I1 | 634 | 2 | Float32 (ABCD) | A | 1272 | inv-10.string_current_1_a | Pending commissioning
273 | INVERTER_10.INV10_String_CURRENT_I2 | 636 | 2 | Float32 (ABCD) | A | 1273 | inv-10.string_current_2_a | Pending commissioning
274 | INVERTER_10.INV10_String_CURRENT_I3 | 638 | 2 | Float32 (ABCD) | A | 1274 | inv-10.string_current_3_a | Pending commissioning
275 | INVERTER_10.INV10_String_CURRENT_I4 | 640 | 2 | Float32 (ABCD) | A | 1275 | inv-10.string_current_4_a | Pending commissioning
276 | INVERTER_10.INV10_String_CURRENT_I5 | 642 | 2 | Float32 (ABCD) | A | 1276 | inv-10.string_current_5_a | Pending commissioning
277 | INVERTER_10.INV10_String_CURRENT_I6 | 644 | 2 | Float32 (ABCD) | A | 1277 | inv-10.string_current_6_a | Pending commissioning
278 | INVERTER_10.INV10_String_CURRENT_I7 | 646 | 2 | Float32 (ABCD) | A | 1278 | inv-10.string_current_7_a | Pending commissioning
279 | INVERTER_10.INV10_String_CURRENT_I8 | 648 | 2 | Float32 (ABCD) | A | 1279 | inv-10.string_current_8_a | Pending commissioning
280 | INVERTER_10.INV10_String_CURRENT_I9 | 650 | 2 | Float32 (ABCD) | A | 1280 | inv-10.string_current_9_a | Pending commissioning
281 | INVERTER_10.INV10_String_CURRENT_I10 | 652 | 2 | Float32 (ABCD) | A | 1281 | inv-10.string_current_10_a | Pending commissioning
282 | INVERTER_10.INV10_String_CURRENT_I11 | 654 | 2 | Float32 (ABCD) | A | 1282 | inv-10.string_current_11_a | Pending commissioning
283 | INVERTER_10.INV10_String_CURRENT_I12 | 656 | 2 | Float32 (ABCD) | A | 1283 | inv-10.string_current_12_a | Pending commissioning
284 | INVERTER_10.INV10_String_CURRENT_I13 | 658 | 2 | Float32 (ABCD) | A | 1284 | inv-10.string_current_13_a | Pending commissioning
285 | INVERTER_10.INV10_String_CURRENT_I14 | 660 | 2 | Float32 (ABCD) | A | 1285 | inv-10.string_current_14_a | Pending commissioning
286 | INVERTER_10.INV10_String_CURRENT_I15 | 662 | 2 | Float32 (ABCD) | A | 1286 | inv-10.string_current_15_a | Pending commissioning
287 | INVERTER_10.INV10_String_CURRENT_I16 | 664 | 2 | Float32 (ABCD) | A | 1287 | inv-10.string_current_16_a | Pending commissioning
288 | INVERTER_10.INV10_String_CURRENT_I17 | 666 | 2 | Float32 (ABCD) | A | 1288 | inv-10.string_current_17_a | Pending commissioning
289 | INVERTER_10.INV10_TOTAL_PRODUCTION | 668 | 2 | Float32 (ABCD) | kWh | 1289 | inv-10.energy_total_kwh | Pending commissioning
290 | Apparent current L1 N | 670 | 2 | Float32 (ABCD) | A | 1290 | pv-meter.current_l1_a | Pending commissioning
291 | Apparent current L2 N | 672 | 2 | Float32 (ABCD) | A | 1291 | pv-meter.current_l2_a | Pending commissioning
292 | Apparent current L3 N | 674 | 2 | Float32 (ABCD) | A | 1292 | pv-meter.current_l3_a | Pending commissioning
293 | Psum3 | 676 | 2 | Float32 (ABCD) | kW | 1293 | neo-01.pv_prod_kw | Ready
294 | Qsum3 | 678 | 2 | Float32 (ABCD) | kvar | 1294 | neo-01.pv_q_kvar | Ready
295 | Real energy L1 L3 delivered | 680 | 2 | Float32 (ABCD) | kWh | 1295 | pv-meter.energy_delivered_kwh | Pending commissioning
296 | Voltage L1 N | 682 | 2 | Float32 (ABCD) | V | 1296 | neo-01.bus_voltage_l1_v | Ready
297 | Voltage L2 N | 684 | 2 | Float32 (ABCD) | V | 1297 | neo-01.bus_voltage_l2_v | Ready
298 | Voltage L3 N | 686 | 2 | Float32 (ABCD) | V | 1298 | neo-01.bus_voltage_l3_v | Ready
299 | Panel Temperature | 688 | 2 | Float32 (ABCD) | °C | 1299 | pv-env.panel_temp_c | Pending commissioning
300 | Pyranometer | 690 | 2 | Float32 (ABCD) | W/m² | 1300 | pv-env.irradiance_wm2 | Pending commissioning
301 | Area_Connection_Error | 692 | 1 | Boolean (uint16 0/1) |  | 1301 | neo-01.pv_logger_comm_fail | Ready
302 | Thermal_Magnetic_Switch_On_(LV PANEL) | 693 | 1 | Boolean (uint16 0/1) |  | 1302 | neo-01.pvcb_closed | Ready
303 | Thermal_Magnetic_Switch_Off (LV PANEL) | 694 | 1 | Boolean (uint16 0/1) |  | 1303 | neo-01.pvcb_open | Ready
304 | Total_Energy | 695 | 2 | Float32 (ABCD) | kWh | 1304 | pv-meter.energy_total_kwh | Pending commissioning